# 7.	INSPECTION AND TEST PROCEDURES

# 7.11.1	Metering Devices, Electromechanical and Solid-State

# Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Verify tightness of electrical connections.

  - Inspect cover gasket, cover glass, condition of spiral spring, disk clearance, contacts, and case-shorting contacts, as applicable.

  - Verify the unit is clean.

  - Verify freedom of movement, end play, and alignment of rotating disk(s).

# Electrical Tests

  - Verify accuracy of meters at all cardinal points.

  - Calibrate meters in accordance with manufacturer’s published data.

  - Verify all instrument multipliers.

  - Verify that current transformer and voltage transformer secondary circuits are intact.

# Test Values – Visual and Mechanical

  - Tightness of electrical connections shall assure a low-resistance connection. (7.11.1.A.3)

# Test Values – Electrical

  - Meter accuracy shall be in accordance with manufacturer’s published data.

  - Calibration results shall be within manufacturer’s published tolerances.

  - Instrument multipliers shall be in accordance with system design specifications.

  - Test results shall confirm the integrity of the secondary circuits of current and voltage transformers.

Page 120

ANSI/NETA ATS-2021