# 7.        INSPECTION AND TEST PROCEDURES

# 7.11.2	Metering Devices, Microprocessor-Based

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect meters and cases for physical damage.

  - Verify the unit is clean.

  - Verify tightness of electrical connections.

  - Record model number, serial number, firmware revision, software revision, and rated control voltage.

  - Verify operation of display and indicating devices.

  - Record passwords.

  - Verify unit is grounded in accordance with manufacturer’s instructions.

  - Verify unit is connected in accordance with manufacturer’s instructions and project drawings.

  - Set all required parameters including instrument transformer ratios, system type, frequency, power demand methods/intervals, and communications requirements.

## Electrical Tests

  - Apply voltage or current as appropriate to each analog input and verify correct measurement and indication.

  - Confirm correct operation and setting of each auxiliary input/output feature in use, including mechanical relay, digital, and analog.

  - After initial system energization, confirm measurements and indications are consistent with loads present in accordance with ANSI/NETA ECS Standard for Electrical Commissioning Specifications for Electrical Power Equipment and Systems.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.11.2	Metering Devices, Microprocessor-Based (continued)

## Test Values – Visual and Mechanical

  - Nameplate data shall be per drawings and specifications. (7.11.2.A.1)

  - Tightness of electrical connections shall assure a low resistance connection. (7.11.2.A.4)

  - Display and indicating devices shall operate per manufacturer’s published data. (7.11.2.A.6)

## Test Values – Electrical

  - Measurement and indication of applied values of voltage and current shall be within manufacturer’s published tolerances for accuracy.

  - All auxiliary input/output features shall operate per settings and manufacturer’s published data.

  - Measurements and indications shall be consistent with energized system loads.