# 7.        INSPECTION AND TEST PROCEDURES

# 7.13	Grounding Systems

## Visual and Mechanical Inspection

  - Verify ground system is in compliance with drawings, specifications, and NFPA 70,

National Electrical Code, Article 250.

  - Inspect physical and mechanical condition.

  - Inspect accessible electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.13.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.13.A.3.1.

  - Perform fall–of–potential or alternative test in accordance with IEEE 81 on the main grounding electrode or system.

  - Perform point-to-point tests to determine the resistance between the main grounding system and all major electrical equipment frames, system neutral, and derived neutral points.

## Test Values – Visual and Mechanical

  - Grounding system electrical and mechanical connections shall be free of corrosion. (7.13.A.2)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.13.A.3.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.13.A.3.2)

7.       INSPECTION AND TEST PROCEDURES

7.13	Grounding Systems (continued)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - The resistance between the main grounding electrode and ground shall be no greater than five ohms for large commercial or industrial systems and one ohm or less for generating or transmission station grounds unless otherwise specified by the owner. (Reference IEEE 142)

  - Investigate point-to-point resistance values that exceed 0.5 ohm.