# 7.       INSPECTION AND TEST PROCEDURES

# 7.15.2 Rotating Machinery, Synchronous Motors and Generators

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Inspect air baffles, filter media, stator windings, stator core, rotor, cooling fans, slip rings, brushes, brush rigging, and bearings.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.15.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Perform special tests such as air-gap spacing and machine alignment.

  - Manually rotate the rotor and check for problems with the bearings or shaft.

  - Rotate the shaft and measure and record the shaft extension runout.

  - Verify the application of appropriate lubrication and lubrication systems.

  - Verify that resistance temperature detector (RTD) circuits conform to drawings.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.15.2.A.5.1.

  - Perform insulation-resistance tests in accordance with IEEE Standard 43.

    - Machines larger than 200 horsepower (150 kilowatts):

Test duration shall be for ten minutes. Calculate polarization index.

    - Machines 200 horsepower (150 kilowatts) and less:

Test duration shall be for one minute. Calculate dielectric-absorption ratio.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.15.2 Rotating Machinery, Synchronous Motors and Generators (continued)

  - On machines rated at 2300 volts and greater perform dielectric withstand voltage tests in accordance with:

    - IEEE Standard 95 for dc dielectric withstand voltage tests.

    - NEMA MG1 for ac dielectric withstand voltage tests.

  - Perform phase-to-phase stator resistance test on machines 2300 volts and greater.

*5.	Perform insulation power-factor or dissipation-factor tests.

*6.	Perform power-factor or dissipation-factor tip-up tests.

*7.	Perform surge comparison tests.

- Perform insulation-resistance test on insulated bearings in accordance with manufacturer’s published data.

- Test surge protection devices in accordance with Section 7.19 and Section 7.20.

- Test motor starter in accordance with Section 7.16.

- Perform resistance tests on resistance temperature detector (RTD) circuits.

- Verify operation of machine space heater.

*13.	Perform vibration test while machine is running under load.

14.	Perform insulation-resistance tests on the main rotating field winding, the exciter-field winding, and the exciter-armature winding in accordance with IEEE Standard 43.

*15.	Perform an ac voltage-drop test on all rotating field poles.

*16.	Perform a high-potential test on the excitation system in accordance with IEEE Standard 421.3.

17.	Measure resistance of machine-field winding, exciter-stator winding, exciter-rotor windings, and field discharge resistors.

*18.	Perform front-to-back resistance tests on diodes and gating tests of silicon-controlled rectifiers for field application semiconductors.

- Prior to re-energizing, apply voltage to the exciter supply and adjust exciter-field current to nameplate value.

- Verify that the field application timer and the enable timer for the power-factor relay have been tested and set to the motor drive manufacturer’s recommended values.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.15.2 Rotating Machinery, Synchronous Motors and Generators (continued)

*21.	Record stator current, stator voltage, and field current for the complete acceleration period including stabilization time for a normally loaded starting condition. From the recording determine the following information:

- Bus voltage prior to start.

- Voltage drop at start.

- Bus voltage at machine full-load.

- Locked-rotor current.

- Current after synchronization but before loading.

- Current at maximum loading.

- Acceleration time to near synchronous speed.

- Revolutions per minute (RPM) just prior to synchronization.

- Field application time.

- Time to reach stable synchronous operation.

*22.	Plot a V–curve of stator current versus excitation current at approximately 50 percent load to check correct exciter operation.

*23.	If the range of exciter adjustment and machine loading permit, reduce excitation to cause power factor to fall below the trip value of the power-factor relay. Verify relay operation.

24.	Measure bearing temperatures while machine is running under load.

*25.	Perform current signature analysis test while machine is running under load.

*26.	Perform partial discharge test.

## Test Values – Visual and Mechanical

  - Inspection (7.15.2.A.4)

    - Air baffles shall be clean and installed in accordance with manufacturer’s published data.

    - Filter media shall be clean and installed in accordance with manufacturer’s published data.

# 7.      INSPECTION AND TEST PROCEDURES

# 7.15.2 Rotating Machinery, Synchronous Motors and Generators (continued)

    - Stator winding shall be clean and show no evidence of overheating, cracking, tracking, or surface partial discharge activity.

    - Stator core shall be clean with no ventilation duct blockage, lamination looseness, burning, or rubs from contact with the rotor.

    - Rotor shall be clean and show no evidence of overheating or cracked bars or end rings and should show no evidence of rubs from contact with the stator.

    - Cooling fans shall operate, not be loose on the rotor shaft, and have no cracks in them.

    - Slip ring alignment shall be within manufacturer’s published tolerances.

    - Brush alignment shall be within manufacturer’s published tolerances.

    - Brush rigging shall be in accordance with manufacturer’s published data.

    - Bearings shall be inspected for evidence of overheating, rubs, rolling element damage, contamination, electrical damage, and lack of lubrication.

  - Compare bolted connection resistance values to values of similar connections. Investigate any values that deviate from similar bolted connections by more than 50 percent of the lowest value. (7.15.2.A.5.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.15.2.A.5.2)

  - Results of thermographic survey shall be in accordance with Section 9. (7.15.2.A.5.3)

  - Air-gap spacing and machine alignment shall be in accordance with manufacturer’s published data. (7.15.2.A.6)

# 7.       INSPECTION AND TEST PROCEDURES

# 7.15.2 Rotating Machinery, Synchronous Motors and Generators (continued)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate any values that deviate from similar bolted connections by more than 50 percent of the lowest value.

  - The recommended minimum insulation resistance (IR 1 min) test results in megohms shall be in accordance with Table 100.11.

    - The polarization index value shall not be less than 2.0.

    - The dielectric absorption ratio shall not be less than 1.4.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand voltage test, the test specimen is considered to have passed the test.

  - Investigate phase-to-phase stator resistance values that deviate by more than five percent.

  - Power-factor or dissipation-factor values shall be compared to manufacturer’s published data. In the absence of manufacturer’s data shall be compared with previous values of similar machines.

  - Tip-up values shall indicate no significant increase in power factor or dissipation factor.

  - If no evidence of distress, insulation failure, or lack of waveform nesting is observed by the end of the total time of voltage application during the surge comparison test, the test specimen is considered to have passed the test.

  - Insulation resistance of bearings shall be within manufacturer’s published tolerances. In the absence of manufacturer’s published tolerances, the comparison shall be made to similar machines.

  - Test results of surge protection devices shall be in accordance with Section 7.19 and Section 7.20.

  - Test results of motor starter equipment shall be in accordance with Section 7.16.

  - RTD circuits shall be in accordance with system design intent and machine protection device manufacturer’s specifications.

  - Heaters shall be operational.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.15.2 Rotating Machinery, Synchronous Motors and Generators (continued)

  - Vibration amplitudes of the uncoupled and unloaded machine shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, vibration amplitudes shall not exceed values shown in Table 100.10. If values exceed those in Table 100.10, perform complete vibration analysis.

  - The recommended minimum insulation resistance (IR 1 min) test results in megohms shall be in accordance with Table 100.11.

  - The pole-to-pole ac voltage drop shall not exceed 10 percent variance between poles.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the winding is considered to have passed the test.

  - The measured resistance values of motor-field windings, exciter-stator windings, exciter- rotor windings, and field-discharge resistors shall be compared to manufacturer’s published data. In the absence of manufacturer’s data, the comparison shall be made to similar machines.

  - Resistance test results of diodes and gating tests of silicon-controlled rectifiers shall be in accordance with industry standards and system design requirements.

  - Exciter power supply shall allow exciter-field current to be adjusted to nameplate value.

  - Application timer and enable timer for power-factor relay test results shall comply with manufacturer’s recommended values.

  - Recorded values shall be in accordance with system design requirements.

  - Plotted V-curve shall indicate correct exciter operation.

  - When reduced excitation falls below trip value for the power-factor relay, the relay shall operate.

  - Verification that bearing temperature detectors are indicating the correct temperatures.

  - Investigate cause if current signature analysis tests show evidence from non-uniform air gaps, rolling element bearing defect, etc. Sideband magnitudes less than 40 dB from the power frequency are considered indicators of broken bars, whereas, magnitudes of less than 60 dB may be a warning of a developing problem. Non-uniform air gaps may be present when the average of the difference between the current magnitudes of the side frequencies from the highest magnitude frequency component are less than 15 dB, and a warning if less than 25 dB.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.15.2 Rotating Machinery, Synchronous Motors and Generators (continued)

  - Perform visual inspections and off-line tests on stator windings if partial discharge levels are high based on comparison to previous tests, tests on similar machines, or values suggested by the test instrument manufacturer.