# 7.       INSPECTION AND TEST PROCEDURES

# 7.15.3 Rotating Machinery, DC Motors and Generators

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Inspect air baffles, filter media, field poles and yokes, armature, cooling fans, commutator, brushes, brush rigging, and bearings.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.15.3.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Inspect commutator and tachometer generator.

*7.	Perform special tests such as air-gap spacing, bar tightness of commutator, and machine alignment.

*8.	If the armature can be manually rotated, check for any obvious problems with the bearings or shaft.

*9.	If the motor shaft can be rotated, measure and record the shaft extension runout.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter, in accordance with Section 7.15.3.A.5.1.

  - Perform insulation-resistance tests on all windings in accordance with IEEE Standard 43.

    - Machines larger than 200 horsepower (150 kilowatts):

Test duration shall be for ten minutes. Calculate polarization index.

    - Machines 200 horsepower (150 kilowatts) and less:

Test duration shall be for one minute. Calculate dielectric absorption ratio for 60/30 second periods.

# 7.      INSPECTION AND TEST PROCEDURES

# 7.15.3 Rotating Machinery, DC Motors and Generators (continued)

*3.	Perform high-potential test in accordance with NEMA MG 1, Section 3.01.

*4.	Perform an ac voltage-drop test on all field poles.

*5.	Perform a surge (impulse) comparison test on the field and armature winding.

*6.	Perform armature commutator bar-to-bar resistance test.

- If the motor has both shunt and series field windings, their relative polarity is to be checked and the leads are to be marked appropriately.

- Measure armature running current and field current or voltage. Compare to nameplate.

*9.	Perform vibration tests while machine is running under load.

10.	Verify that all protective devices are in accordance with Section 7.16.

## Test Values – Visual and Mechanical

  - Inspection (7.15.3.A.4)

    - Air baffles shall be clean and installed in accordance with manufacturer’s published data.

    - Filter media shall be clean.

    - Field poles and yokes shall show no evidence of overheating, contamination, or other defects.

    - The armature and commutator shall show no evidence of overheating, contamination, or other defect.

    - Cooling fans shall operate.

    - Commutator runout shall be within manufacturer’s published tolerances.

    - Brush alignment shall be within manufacturer’s published tolerances.

    - Brush rigging shall be in accordance with manufacturer’s published data.

    - Bearings shall be inspected for evidence of overheating, rubs, rolling element damage contamination, electrical damage, and lack of lubrication.

  - Compare bolted connection resistance values to values of similar connections. Investigate any values that deviate from similar bolted connections by more than 50 percent of the lowest value. (7.15.3.A.5.1)

# 7.       INSPECTION AND TEST PROCEDURES

# 7.15.3 Rotating Machinery, DC Motors and Generators (continued)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.15.3.A.5.2)

  - Results of thermographic survey shall be in accordance with Section 9. (7.15.3.A.5.3)

  - Commutator and tachometer generator shall be in accordance with manufacturer’s published data and system design. (7.15.3.A.6)

  - Air-gap spacing and machine alignment shall be in accordance with manufacturer’s published data. (7.15.3.A.7)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate any values that deviate from similar bolted connections by more than 50 percent of the lowest value.

  - The recommended minimum insulation resistance (IR 1 min) test results in megohms shall be in accordance with Table 100.11.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the winding is considered to have passed the test.

  - The individual pole-to-pole ac voltage drop shall not exceed ten percent variance from the average value (average value = test voltage divided by number of coils) applicable to all of the poles.

  - Measured running current and field current or voltage shall be comparable to nameplate data.

  - Vibration amplitudes of the uncoupled and unloaded machine shall not exceed values shown in Table 100.10. If values exceed those in Table 100.10, perform complete vibration analysis.

  - Test results of motor starter equipment shall be in accordance with Section 7.16.

  - Investigate bar-to-bar resistance values of armature that deviate by more than five percent.