# 7.       INSPECTION AND TEST PROCEDURES

# 7.16.1.2	Motor Control, Motor Starters, Medium-Voltage

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.16.1.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Test electrical and mechanical interlock systems for correct operation and sequencing.

  - Verify correct barrier and shutter installation and operation.

  - Exercise active components and confirm correct operation of indicating devices.

  - Inspect contactors.

    - Verify mechanical operation.

    - Verify contact gap, wipe, alignment, and pressure are in accordance with manufacturer’s published data.

  - Verify overload protection rating is correct for its application. Set adjustable or programmable devices according to the protective device coordination study.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.16.1.2	Motor Control, Motor Starters, Medium-Voltage (continued)

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.16.1.2.A.5.1.

  - Perform insulation-resistance tests on contactor(s) for one minute, phase-to-ground and phase-to-phase with the contactor closed, and across each open contact. Test voltage shall be in accordance with manufacturer’s published data, or Table 100.1.

*3.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

*4.	Perform magnetron atmospheric condition (MAC) test on each vacuum interrupter.

*5.	Perform a dielectric withstand voltage test in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.9.

- Perform vacuum bottle integrity test (dielectric withstand voltage) across each vacuum bottle with the contacts in the open position in strict accordance with manufacturer’s published data.

- Perform contact resistance tests.

- Measure blowout coil circuit resistance.

- Measure resistance of power fuses.

- Energize contactor using an auxiliary source. Adjust armature to minimize operating vibration.

- Test control power transformers in accordance with Section 7.1.B.8.

- Test starting transformers, in accordance with Section 7.2.1.

- Test starting reactors, in accordance with 7.20.3.

- Test motor protection devices in accordance with manufacturer’s published data. In the absence of manufacturer’s data, test in accordance with Section 7.9.

*15.	Perform system function test in accordance with ANSI/NETA ECS Standard for Electrical Commissioning Specifications for Electrical Power Equipment & Systems.

- Verify operation of cubicle space heater.

- Test instrument transformers in accordance with Section 7.10.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.16.1.2	Motor Control, Motor Starters, Medium-Voltage (continued)

- Test metering devices in accordance with Section 7.11.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.16.1.2.A.5.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.16.1.2.A.5.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.16.1.2.A.5.3)

  - Electrical and mechanical interlocks shall operate in accordance with system design. (7.16.1.2.A.6)

  - Barrier and shutter installation and operation shall be in accordance with manufacturer’s design. (7.16.1.2.A.7)

  - Indicating devices shall operate in accordance with system design. (7.16.1.2.A.8)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.5. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - Evaluate each vacuum interrupter in accordance with test equipment manufacturer’s instructions. In the absence of manufacturer’s published data, each vacuum interrupter pressure shall not be greater than 1x10-2 Pa and shall not deviate from adjacent poles by more than two orders of magnitude.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand voltage test, the test specimen is considered to have passed the test.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the vacuum bottle integrity test, the vacuum bottle is considered to have passed the test.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.16.1.2	Motor Control, Motor Starters, Medium-Voltage (continued)

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. If manufacturer’s published data is not available, investigate values which deviate from those of similar connections by more than 50 percent of the lowest value.

  - Resistance values of blowout coils shall be in accordance with manufacturer’s published data.

  - Resistance values shall not deviate by more than 15 percent between identical fuses.

  - Contactor coil shall operate with minimal vibration and noise.

  - Control power transformer test results shall be in accordance with Section 7.1.D.8.

  - Starting transformer test results shall be in accordance with Section 7.2.1.

  - Starting reactor test results shall be in accordance with Section 7.20.3.

  - Motor protection parameters shall be in accordance with manufacturer’s published data.

  - System function test results shall be in accordance with manufacturer’s published data and system design.

  - Heaters shall be operational.

  - The results of instrument transformer tests shall be in accordance with Section 7.10.

  - Metering device test results shall be in accordance with Section 7.11.