# 7.       INSPECTION AND TEST PROCEDURES

# 7.18.1.2	Direct-Current Systems, Batteries, Vented Nickel-Cadmium

## Visual and Mechanical Inspection

  - Verify that batteries are adequately located.

  - Verify that battery area ventilation system is operable.

  - Verify existence of suitable eyewash equipment.

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Verify adequacy of battery support racks or cabinets, mounting, battery spill containment system, anchorage, alignment, grounding, and clearances.

  - Verify electrolyte level. Measure pilot-cell electrolyte temperature.

  - Verify the units are clean.

  - Verify application of an oxide inhibitor on battery terminal connections.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.18.1.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

## Electrical Tests

  - Perform resistance measurements through all bolted connections with a low-resistance ohmmeter in accordance with Section 7.18.1.2.A.10.1.

  - Measure charger float and equalizing voltage levels. Adjust to battery manufacturer’s recommended settings.

  - Verify all charger functions and alarms.

  - Measure each cell voltage and total battery voltage with charger energized and in float mode of operation.

  - Measure intercell connection resistances.

# 7.         INSPECTION AND TEST PROCEDURES

# 7.18.1.2	Direct-Current Systems, Batteries, Vented Nickel-Cadmium (continued)

  - Perform a load test in accordance with manufacturer’s published data or IEEE 1106.

  - Measure the battery system voltage from positive to-ground and negative-to-ground.

## Test Values – Visual and Mechanical

  - Electrolyte level shall be within normal limits. (7.18.1.2.A.7)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.18.1.2.A.10.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.18.1.2.A.10.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.18.1.2.A.10.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Charger float and equalize voltage levels shall be in accordance with battery manufacturer’s published data.

  - The results of charger functions and alarms shall be in accordance with manufacturer’s published data.

  - Cell voltages shall be within 0.05 volt of each other or in accordance with manufacturer’s published data.

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value

  - Results of load tests shall be in accordance with manufacturer’s published data or IEEE 1106.

  - Voltage measured from positive to ground shall be equal in magnitude to the voltage measured from negative to ground.