# 7.       INSPECTION AND TEST PROCEDURES

# 7.19.2	Surge Arresters, Medium- and High-Voltage

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, grounding, and clearances.

  - Verify the arresters are clean.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.19.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

  - Verify that the ground lead on each device is individually attached to a ground bus or ground electrode.

  - Verify that the stroke counter is correctly mounted and electrically connected.

  - Record the stroke counter reading.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.19.2.A.5.1.

  - Perform an insulation-resistance test on each arrester, phase terminal-to-ground. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Test grounding connection in accordance with Section 7.13.

*4.	Perform a watts-loss test.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.19.2.A.5.1)

# 7.        INSPECTION AND TEST PROCEDURES

# 7.19.2	Surge Arresters, Medium- and High-Voltage (continued)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.19.2.A.5.2)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation –resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Resistance between the arrester ground terminal and the ground system shall be less than 0.5 ohm and in accordance with Section 7.13.

  - Watts-loss values are evaluated on a comparison basis with similar units and test equipment manufacturer’s published data.