# 7.        INSPECTION AND TEST PROCEDURES

# 7.2.1.1	Transformers, Dry-Type, Air-Cooled, Low-Voltage, Small

NOTE: This category consists of power transformers with windings rated 600 volts or less and sizes equal to or less than 167 kVA single-phase or 500 kVA three phase.

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify that resilient mounts are free and that any shipping brackets have been removed.

  - Verify the unit is clean.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.2.1.1.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify that as-left tap connections are as specified.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.2.1.1.A.6.1.

  - Perform insulation-resistance tests winding-to-winding and each winding-to-ground. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.5. Calculate dielectric absorption ratio.

*3.	Perform turns-ratio tests at the designated tap position.

4. Verify correct secondary voltage phase-to-phase and phase-to-neutral after energization and prior to loading.

# 7.     INSPECTION AND TEST PROCEDURES

# 7.2.1.1	Transformers, Dry-Type, Air-Cooled, Low-Voltage, Small (continued)

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.2.1.1.A.6.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.2.1.1.A.6.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.2.1.1.A.6.3)

  - Tap connections are left as found unless otherwise specified. (7.2.1.1.A.7)

## Test Values – Electrical

  - Compare bolted electrical connection resistances to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Minimum insulation-resistance values of transformer insulation shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.5. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. The dielectric absorption ratio shall not be less than 1.0.

  - Turns-ratio test results shall not deviate by more than one-half percent from either the adjacent coils or the calculated ratio.

  - Phase-to-phase and phase-to-neutral secondary voltages shall be in agreement with nameplate data.