# 7. INSPECTION AND TEST PROCEDURES

# 7.2.1.2	Transformers, Dry-Type, Air-Cooled, Large

NOTE: This category consists of power transformers with windings rated higher than 600 volts and low-voltage transformers larger than 167 kVA single-phase or 500 kVA three-phase.

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify that resilient mounts are free and that any shipping brackets have been removed.

  - Verify the unit is clean.

*6.	Verify that control and alarm settings on temperature indicators are as specified.

- Verify that cooling fans operate and that fan motors have correct overcurrent protection.

- Inspect bolted electrical connections for high resistance using one or more of the following methods:

  - Use of a low-resistance ohmmeter in accordance with Section 7.2.1.2.B.1.

  - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

  - Perform thermographic survey in accordance with Section 9.

- Perform specific inspections and mechanical tests as recommended by the manufacturer.

- Verify that as-left tap connections are as specified.

- Verify the presence of surge arresters.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.2.1.2.A.8.1.

# 7.      INSPECTION AND TEST PROCEDURES

# 7.2.1.2 Transformers, Dry-Type, Air-Cooled, Large (continued)

  - Perform insulation-resistance tests winding-to-winding and each winding-to-ground. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data use Table 100.5. Calculate dielectric absorption ratio and polarization index.

  - Perform power-factor or dissipation-factor tests on all windings in accordance with the test equipment manufacturer’s published data.

*4.	Perform a power-factor or dissipation-factor tip-up test on windings greater than 2.5 kV.

5.	Perform turns-ratio tests at all tap positions.

*6.	Perform an excitation-current test on each phase.

*7.	Measure the resistance of each winding at each tap connection. Test current not to exceed 10% of rated current.

8.	Measure core insulation resistance at 500 volts dc if the core is insulated and the core ground strap is removable.

*9.	Perform an applied voltage test on all high- and low-voltage windings-to-ground. See IEEE C57.12.91, Sections 10.2 and 10.9.

- Verify correct secondary voltage, phase-to-phase and phase-to-neutral, after energization and prior to loading.

- Test surge arresters in accordance with Section 7.19.

*12.	Perform online partial-discharge survey on windings rated higher than 1000 volts in accordance with Section 11.

## Test Values – Visual and Mechanical

  - Control and alarm settings on temperature indicators shall operate within manufacturer’s recommendations for specified settings. (7.2.1.2.A.6)

  - Cooling fans shall operate. (7.2.1.2.A.7)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.2.1.2.A.8.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.2.1.2.A.8.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.2.1.2.A.8.3)

  - Tap connections shall be left as found unless otherwise specified. (7.2.1.2.A.10)

# 7.       INSPECTION AND TEST PROCEDURES

# 7.2.1.2	Transformers, Dry-Type, Air-Cooled, Large (continued)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Minimum insulation-resistance values of transformer insulation shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.5. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. The dielectric absorption ratio and polarization index shall not be less than 1.0.

  - The following values are typical for insulation power factor tests:

    - CHL Power transformers: 2.0 percent or less.

    - CHL Distribution transformers: 5.0 percent or less

    - CH and CL power-factor or dissipation-factor values will vary due to support insulators and bus work utilized on dry transformers. Consult transformer manufacturer’s or test equipment manufacturer’s data for additional information.

  - Power-factor or dissipation-factor tip-up exceeding 1.0 percent shall be investigated.

  - Turns-ratio test results shall not deviate more than one-half percent from either the adjacent coils or the calculated ratio.

  - The typical excitation current test data pattern for a three-legged core transformer is two similar current readings and one lower current reading. The test should produce a pattern typical for the specific transformer type and configuration.

  - Temperature-corrected winding-resistance values shall compare within one percent of previously obtained results.

  - Core insulation-resistance values shall not be less than one megohm at 500 volts dc.

  - AC dielectric withstand test voltage shall not exceed 75 percent of factory test voltage for one minute duration. DC dielectric withstand test voltage shall not exceed 100 percent of the ac rms test voltage specified in IEEE C57.12.91, Section 10.2 for one minute duration. If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand voltage test, the test specimen is considered to have passed the test.

  - Phase-to-phase and phase-to-neutral secondary voltages shall be in agreement with nameplate data.

# 7.      INSPECTION AND TEST PROCEDURES

# 7.2.1.2	Transformers, Dry-Type, Air-Cooled, Large (continued)

  - Test results for surge arresters shall be in accordance with Section 7.19.

  - Results of online partial-discharge survey should be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.23.