# 7.        INSPECTION AND TEST PROCEDURES

# 7.2.2	Transformers, Liquid-Filled

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect impact recorder prior to unloading.

*4.	Test dew point of tank gases.

- Inspect anchorage, alignment, and grounding.

- Verify the presence of PCB content labeling.

- Verify removal of any shipping bracing after placement.

- Verify the bushings are clean.

- Verify that alarm, control, and trip settings on temperature and level indicators are as specified.

- Verify operation of alarm, control, and trip circuits from temperature and level indicators, pressure relief device, gas accumulator, and fault pressure relay.

- Verify that cooling fans and pumps operate correctly and have appropriate overcurrent protection.

- Inspect bolted electrical connections for high resistance using one or more of the following methods:

  - Use of a low-resistance ohmmeter in accordance with Section 7.2.2.B.1.

  - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

  - Perform thermographic survey in accordance with Section 9.

- Verify correct liquid level in tanks and bushings.

- Verify valves are in the correct operating position.

- Verify that positive pressure is maintained on gas-blanketed transformers.

- Perform inspections and mechanical tests as recommended by the manufacturer.

- Test load tap-changer in accordance with Section 7.12.3.

# 7.  INSPECTION AND TEST PROCEDURES

# 7.2.2	Transformers, Liquid-Filled (continued)

- Verify presence of transformer surge arresters.

- Verify de-energized tap-changer position is left as specified.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.2.2.A.12.1.

  - Perform insulation-resistance tests, winding-to-winding and each winding-to-ground. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.5. Calculate dielectric absorption ratio and polarization index.

  - Perform turns-ratio tests at all tap positions.

  - Perform insulation power-factor or dissipation-factor tests on all windings in accordance with test equipment manufacturer’s published data.

  - Perform power-factor or dissipation-factor tests on each bushing equipped with a power- factor/ capacitance tap. In the absence of a power-factor/capacitance tap, perform hot-collar tests. These tests shall be in accordance with the test equipment manufacturer’s published data.

  - Perform excitation-current tests in accordance with test equipment manufacturer’s published data.

*7.	Perform sweep frequency response analysis tests.

8.	Measure the resistance of each winding at each tap connection. Test current not to exceed 10 percent rated current according to IEEE C57.152.

*9.	Perform dynamic resistance measurement for load tap changer.

*10.	Perform leakage reactance three phase equivalent and per phase tests.

*11.	If core ground strap is accessible, remove and measure core insulation resistance at 500 volts dc.

*12.	Measure the percentage of oxygen in the gas blanket.

*13. Perform dielectric frequency response test in accordance with test equipment manufacturer’s published data.

7.          INSPECTION AND TEST PROCEDURES

    - Transformers, Liquid-Filled (continued)

      - Remove a sample of insulating liquid in accordance with ASTM D923. Sample shall be tested for the following.

        - Dielectric breakdown voltage: ASTM D1816

        - Acid neutralization number: ASTM D974

*3	Specific gravity: ASTM D1298

- Interfacial tension: ASTM D971

- Color: ASTM D1500

- Visual Condition: ASTM D1524

- Water in insulating liquids: ASTM D1533.

*8.	Power factor or dissipation factor in accordance with ASTM D924.

      - Remove a sample of insulating liquid in accordance with ASTM D923 and perform dissolved-gas analysis (DGA) in accordance with IEEE C57.104 or ASTM D3612.

      - Test instrument transformers in accordance with Section 7.10.

      - Test surge arresters in accordance with Section 7.19.

      - Test transformer neutral grounding impedance device.

      - Verify operation of cubicle or air terminal compartment space heaters.

## Test Values – Visual and Mechanical

  - Alarm, control, and trip circuits from temperature and level indicators as well as pressure relief device and fault pressure relay shall operate within manufacturer’s recommendations for their specified settings. (7.2.2.A.10)

  - Cooling fans and pumps shall operate. (7.2.2.A.11)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.2.2.A.12.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.2.2.A.12.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.2.2.A.12.3)

# 7.        INSPECTION AND TEST PROCEDURES

# 7.2.2	Transformers, Liquid-Filled (continued)

  - Liquid levels in the transformer tanks and bushings shall be within indicated tolerances. (7.2.2.A.13)

  - Positive pressure shall be indicated on pressure gauge for gas-blanketed transformers. (7.2.2.A.15)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Minimum insulation-resistance values of transformer insulation shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.5. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. The polarization index shall not be less than 1.0.

  - Turns-ratio test results shall not deviate by more than one-half percent from either the adjacent coils or the calculated ratio.

  - Maximum insulation power-factor/dissipation-factor values of liquid-filled transformers corrected to 20ºC shall be in accordance with the manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.3. Distribution transformer power factor results shall compare to previously obtained results.

  - Investigate bushing power-factor values that vary from nameplate values by more than 50 percent. Investigate bushing capacitance values that vary from nameplate values by more than five percent. Investigate bushing hot-collar test values that exceed 0.1 Watts.

  - The typical excitation-current test data pattern for a three-legged core transformer is two similar current readings and one lower current reading. The test should produce a pattern typical for the specific transformer type and configuration.

  - Sweep frequency response analysis test results should compare to factory and previous test results.

  - Temperature corrected winding-resistance values shall compare within two percent of previously obtained results or between adjacent phases.

  - Dynamic resistance measurements results shall compare to factory and previous test results.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.2.2	Transformers, Liquid-Filled (continued)

  - Investigate leakage reactance three phase equivalent test results that deviate from the nameplate by more than 3%. The per phase test results serve as a benchmark for future tests and should not deviate from the average of the three readings by more than 3%.

  - Core insulation resistance values shall be comparable to the factory test value but not less than 500 megohms at 500 volts dc.

  - Investigate the presence of oxygen in the nitrogen gas blanket.

  - Dielectric frequency response analysis should compare to factory and previous test results.

  - Insulating liquid values shall be in accordance with Table 100.4.

  - Evaluate results of dissolved-gas analysis in accordance with IEEE C57.104.

  - Results of electrical tests on instrument transformers shall be in accordance with Section 7.10.

  - Results of surge arrester tests shall be in accordance with Section 7.19.

  - Compare grounding impedance device values to manufacturer’s published data.

  - Heaters shall be operational.