# 7.       INSPECTION AND TEST PROCEDURES

# 7.20.1	Capacitors and Reactors, Capacitors (continued)

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, grounding, and clearances.

  - Verify the unit is clean.

  - Verify that capacitors are electrically connected in their specified configuration.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.20.1.B.1.

    - Verify tightness of accessible-bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter. See Section 7.20.1.A.6.1.

  - Perform insulation-resistance tests from phase terminal(s) to case for one minute. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Measure the capacitance of all terminal combinations.

  - Measure resistance of the internal discharge resistors.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.20.1.A.6.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.20.1.A.6.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.20.1.A.6.3)

# 7.       INSPECTION AND TEST PROCEDURES

# 7.20.1	Capacitors and Reactors, Capacitors (continued)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table for manufacturer’s recommendations should be investigated.

  - Investigate capacitance values differing from manufacturer’s published data.

  - Investigate discharge resistor values differing from manufacturer’s published data. In accordance with NFPA 70, Article 460, residual voltage of a capacitor shall be reduced to 50 volts in the following time intervals after being disconnected from the source of supply:

Rated Voltage

 600 volts

> 600 volts

Discharge Time 1 minute

5 minutes