# 7.       INSPECTION AND TEST PROCEDURES

# 7.21	Outdoor Bus Structures

## Visual and Mechanical Inspection

  - Compare bus arrangement with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the support insulators are clean.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.21.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.21.A.5.1.

  - Measure insulation resistance of each bus, phase-to-ground with other phases grounded for equipment rated less than 46 kV. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.1.

  - Perform dielectric withstand voltage test on each bus phase, phase-to-ground with other phases grounded. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.19. Test duration shall be for one minute.

*4.	Perform insulation power-factor or dissipation-factor tests on each bus phase, phase-to- ground with other phases grounded.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.21.A.5.1)

7.        INSPECTION AND TEST PROCEDURES

7.21	Outdoor Bus Structures (continued)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.12. (7.21.A.5.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.21.A.5.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.1.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand voltage test, the test specimen is considered to have passed the test.

  - Insulation power-factor or dissipation-factor results shall be compared to manufacturer’s published data. In absence of manufacturer’s published data, the comparison shall be made to previous test results or data from the test equipment manufacturers.