# 7.       INSPECTION AND TEST PROCEDURES

# 7.22.2	Emergency Systems, Uninterruptible Power Systems

NOTE: There are many configurations of uninterruptible power supply installations. Some are as simple as a static switch selecting between two highly reliable sources, while others are complex systems using a combination of rectifiers, batteries, inverters, motor/generators, static switches, and bypass switches. It is the intent of these specifications to list possible tests of the major components of the system and more specifically the system as a whole. It is important that the manufacturer’s recommended commissioning tests be performed.

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, grounding, and required clearances.

  - Verify that fuse sizes and types correspond to drawings.

  - Verify the unit is clean.

  - Test all electrical and mechanical interlock systems for correct operation and sequencing.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.22.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify operation of forced ventilation.

  - Verify that filters are in place and/or vents are clear.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.22.2.A.7.1.

  - Test static transfer from inverter to bypass and back. Use normal load, if possible.

  - Set free running frequency of oscillator.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.22.2	Emergency Systems, Uninterruptible Power Systems (continued)

  - Test dc undervoltage trip level on inverter input breaker. Set according to manufacturer’s published data.

  - Test alarm circuits.

  - Verify synchronizing indicators for static switch and bypass switches.

  - Perform electrical tests for UPS system breakers in accordance with Section 7.6.

  - Perform electrical tests for UPS system automatic transfer switches in accordance with Section 7.22.3.

  - Perform electrical tests for UPS system batteries in accordance with Section 7.18.

  - Perform electrical tests for UPS rotating machinery in accordance with Section 7.15.

## Test Values – Visual and Mechanical

  - Electrical and mechanical interlock systems shall operate in accordance with system design requirements. (7.22.2.A.6)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.22.2.A.7.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.12. (7.22.2.A.7.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.22.2.A.7.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Static transfer shall function in accordance with manufacturer’s published data.

  - Oscillator free running frequency shall be within manufacturer’s published tolerances.

  - DC undervoltage shall trip inverter input breaker.

  - Alarm circuits shall operate in accordance with design requirements.

  - Synchronizing indicators shall operate in accordance with design requirements.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.22.2	Emergency Systems, Uninterruptible Power Systems (continued)

  - Breaker performance shall be in accordance with Section 7.6.1.

  - Automatic transfer switch performance shall be in accordance with Section 7.22.3.

  - Battery test results shall be in accordance with Section 7.18.

  - Rotating machinery performance shall be in accordance with Section 7.15.