# 7.       INSPECTION AND TEST PROCEDURES

# 7.22.3	Emergency Systems, Automatic Transfer Switches

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, grounding, and required clearances.

  - Verify the unit is clean.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

  - Verify that manual transfer warnings are attached and visible.

  - Verify tightness of all control connections.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.22.3.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Perform manual transfer operation.

  - Verify positive mechanical interlocking between normal and alternate sources.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.22.3.A.8.1.

  - Perform insulation resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with switch in both source positions and across each open pole. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.1.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.22.3	Emergency Systems, Automatic Transfer Switches (continued)

*3.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components or for control devices that cannot tolerate the applied voltage, follow manufacturer’s recommendation.

- Perform a contact/pole-resistance test.

- Verify settings and operation of control devices.

- Calibrate and set all relays and timers in accordance with Section 7.9

- Verify phase rotation, phasing, and synchronized operation as required by the application.

- Verify correct operation and timing of the following functions:

  - Normal source voltage-sensing and frequency-sensing relays.

  - Engine start sequence.

  - Time delay upon transfer.

  - Alternate source voltage-sensing and frequency-sensing relays.

  - Automatic transfer operation.

  - Interlocks and limit switch function.

  - Time delay and retransfer upon normal power restoration.

  - Engine cool down and shutdown feature.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.22.3.A.8.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.12. (7.22.3.A.8.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.22.3.A.8.3)

# 7.       INSPECTION AND TEST PROCEDURES

# 7.22.3	Emergency Systems, Automatic Transfer Switches (continued)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation resistance values of transfer switches shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations shall be investigated.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. If manufacturer’s published data is not available, investigate values that deviate from adjacent poles or similar switches by more than 50 percent of the lowest value.

  - Control devices shall operate in accordance with manufacturer’s published data.

  - Relay test results shall be in accordance with Section 7.9.

  - Phase rotation phasing, and synchronization shall be in accordance with system design specifications.

  - Operation and timing shall be in accordance with manufacturer’s and system design requirements.