# 7.       INSPECTION AND TEST PROCEDURES

# 7.23	Communications

## Visual and Mechanical Inspection

  - Record model numbers, style numbers, serial numbers, firmware revisions, software revisions, and rated control voltage.

  - Inspect the physical and mechanical condition of equipment and wiring.

  - Verify operation of light-emitting diodes, displays, and targets.

  - Verify equipment is clean.

  - Check tightness of all connections.

  - Verify appropriate grounding equipment and circuits.

  - Verify backup batteries are healthy and connected.

  - Check with setting engineer for applicable firmware updates and product recalls.

  - Verify settings and application configurations are in accordance with engineered settings.

  - Verify devices display the correct date and time.

  - Reset and clear events, maintenance data, statistical data, and alarms from the devices after any tests.

  - Download or document settings and logic from the devices.

## Electrical Tests

  - Perform metering tests on all analog inputs and verify metering values on the human machine interface (HMI) and at remote terminals.

  - Verify operation of all enabled digital inputs.

  - Verify operation of all digital outputs by operating the controlled device.

  - Verify all communication links are operational and function test failovers of redundant communication links.

  - Verify operation of all internal logic functions including tagging, lockouts, and local/remote control.

  - Verify alarm and status points.

  - Verify deadband and zero deadband settings and operation.

7.        INSPECTION AND TEST PROCEDURES

7.23	Communications (continued)

  - Reset and clear events, maintenance data, statistical data, and alarms from the devices after completion of tests.

## Test Values – Visual and Mechanical

  - Light-emitting diodes, displays, and targets should illuminate.

  - Equipment shall be clean and operational.

  - Settings and logic shall agree with the most recent engineered setting files.

  - Verify equipment displays the correct date and time and events are accurately timestamp.

## Test Values – Electrical

  - Metering readings shall be in accordance with manufacturer’s published tolerances.

  - Inputs shall operate as per the design.

  - Outputs shall operate as per the design.

  - Communication links shall be operational and failover times shall be in accordance with the manufacturer’s published data.

  - Internal logic functions shall operate as per the design.

  - Alarms and statuses shall be as per the design.

  - Deadbands shall operate in accordance with manufacturer’s published data.

  - Indications and statistical data shall operate in accordance with manufacturer’s published data.