# 7.        INSPECTION AND TEST PROCEDURES

# 7.24.2 Automatic Circuit Reclosers and Line Sectionalizers, Automatic Line Sectionalizers, Oil (continued)

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

  - Perform all mechanical operation and contact alignment tests on both the sectionalizer and its operating mechanism in accordance with manufacturer’s published data.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.24.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify appropriate insulating liquid level.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.24.2.A.6.1.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with sectionalizer closed, and across each open pole. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.1.

  - Perform a contact/pole-resistance test.

  - Remove a sample of insulating liquid in accordance with ASTM D923. The sample shall be tested in accordance with the referenced standard.

    - Dielectric breakdown voltage: ASTM D877

    - Color: ASTM D 1500

    - Visual condition: ASTM D 1524

# 7.        INSPECTION AND TEST PROCEDURES

# 7.24.2 Automatic Circuit Reclosers and Line Sectionalizers, Automatic Line Sectionalizers, Oil (continued)

  - Perform dielectric withstand voltage tests on each pole-to-ground and pole-to-pole with recloser in closed position.

  - Test sectionalizer counting function by application of simulated fault current (greater than 160 percent of continuous current rating).

  - Test sectionalizer lockout function for all counting positions.

  - Test for reset timing on trip actuator.

*9.	Perform power-factor or dissipation-factor tests on each pole with the recloser open and each phase with the recloser closed.

*10.	Perform power-factor or dissipation-factor tests on each bushing equipped with a power- factor/ capacitance tap. In the absence of a power-factor/capacitance tap, perform hot-collar tests. These tests shall be in accordance with the test equipment manufacturer’s published data.

## Test Values – Visual and Mechanical

  - Mechanical operation and contact alignment shall be in accordance with manufacturer’s published data. (7.24.2.A.5)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.24.2.A.6.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.12. (7.24.2.A.6.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.24.2.A.6.3)

  - Insulating liquid level shall be in accordance with manufacturer’s recommended tolerances. (7.24.2.A.7)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.24.2 Automatic Circuit Reclosers and Line Sectionalizers, Automatic Line Sectionalizers, Oil (continued)

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. If manufacturer’s published data is not available, investigate values that deviate from adjacent poles or similar switches by more than 50 percent of the lowest value.

  - Insulating liquid test results shall be in accordance with Table 100.4.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the test specimen is considered to have passed the test.

  - Operations counter shall advance one digit per close-open cycle.

  - Lockout function shall operate in accordance with manufacturer’s published data.

  - Reset timing of trip actuator shall operate in accordance with manufacturer’s published data.

  - Power-factor or dissipation-factor values and tank loss-index shall be compared to manufacturer’s published data. In the absence of manufacturer’s published data, the comparison shall be made to test data from similar sectionalizers or data from test equipment manufacturers.

  - Power-factor or dissipation-factor and capacitance values shall be within ten percent of nameplate rating for bushings. Hot collar tests are evaluated on a milliampere/milliwatt loss basis, and the results should be compared to values of similar bushings.