# 7.      INSPECTION AND TEST PROCEDURES

# 7.5.1.3	Switches, Air, Medium- and High-Voltage, Open

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, grounding, and required clearances.

  - Verify the unit is clean.

  - Perform mechanical operator tests in accordance with manufacturer’s published data.

  - Verify correct operation and adjustment of motor operator limit switches and mechanical interlocks.

  - Verify correct blade alignment, blade penetration, travel stops, arc interrupter operation, and mechanical operation.

  - Verify operation and sequencing of interlocking systems.

  - Verify that each fuse has adequate mechanical support and contact integrity.

  - Verify that fuse sizes and types are in accordance with drawings, short-circuit study, and coordination study.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.5.1.3.B.1.

    - Verify tightness of accessible-bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify correct operation of all indicating and control devices.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

  - Record as-found and as-left operation counter readings.

# 7.      INSPECTION AND TEST PROCEDURES

# 7.5.1.3	Switches, Air, Medium- and High-Voltage, Open (continued)

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low resistance ohmmeter, in accordance with Section 7.5.1.3.A.11.1.

  - Perform contact-resistance test across each switchblade and fuseholder.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with switch closed, and across each open pole. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

*4.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components or control devices that cannot tolerate the applied voltage, follow manufacturer’s recommendation.

- Perform a dielectric withstand voltage test on each pole with switch closed. Test each pole- to-ground with all other poles grounded. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.19.

- Measure fuse resistance.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.5.1.3.1.11.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.5.1.3.A.11.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.5.1.3.A.11.3)

  - Operation counter should advance one digit per close-open cycle. (7.5.1.3.A.14)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer's published data. If manufacturer's data is not available, investigate values that deviate from adjacent poles or similar switches by more than 50 percent of the lowest value.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.5.1.3	Switches, Air, Medium- and High-Voltage, Open (continued)

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. Dielectric withstand voltage tests should not proceed until insulation-resistance levels are raised above minimum values.

  - Minimum insulation-resistance values of control wiring shall not be less than two megohms.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand voltage test, the test specimen is considered to have passed the test.

  - Investigate fuse resistance values that deviate from each other by more than 15 percent.