# 7.        INSPECTIONS AND TEST PROCEDURES

# 7.5.4	Switches, SF6, Medium-Voltage

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, grounding, and required clearances.

  - Verify the unit is clean.

  - Inspect and service mechanical operator and SF6 gas insulated system in accordance with the manufacturer’s published data.

  - Verify correct operation of SF6 gas pressure alarms and limit switches, as recommended by the manufacturer.

  - Measure critical distances as recommended by the manufacturer.

  - Verify operation and sequencing of interlocking systems.

  - Verify that each fuse holder has adequate mechanical support and contact integrity.

  - Verify that fuse sizes and types are in accordance with drawings, short-circuit study, and coordination study.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.5.4.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify appropriate lubrication on moving, current-carrying parts and on moving and sliding surfaces.

  - Test for SF6 gas leaks in accordance with manufacturer’s published data.

  - Record as-found and as-left operation counter readings.

# 7.        INSPECTIONS AND TEST PROCEDURES

# 7.5.4	Switches, SF6, Medium-Voltage (continued)

## Electrical Tests

  - Perform resistance measurements through accessible bolted electrical connections with a low-resistance ohmmeter. See Section 7.5.4.A.11.1.

  - Perform a contact/pole-resistance test.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with switch closed, and across each open pole. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

*4.	Remove a sample of SF6 gas if provisions are made for sampling and test in accordance with Table 100.13.

5.  Perform a dielectric withstand voltage test across each gas bottle with the switch in the open position in accordance with manufacturer’s published data.

*6.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

- Perform a dielectric withstand voltage test in accordance with manufacturer’s published data.

- Verify open and close operation from control devices.

- Measure fuse resistance.

## Test Values – Visual and Mechanical

  - Critical distances of operating mechanism shall be in accordance with manufacturer’s published data. (7.5.4.A.7)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.5.4.A.11.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.5.4.A.11.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.5.4.A.11.3)

  - Operation counter shall advance one digit per close-open cycle. (7.5.4.A.14)

# 7.        INSPECTIONS AND TEST PROCEDURES

# 7.5.4	Switches, SF6, Medium-Voltage (continued)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer's published data. If manufacturer's data is not available, investigate values that deviate from adjacent poles or similar switches by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. Dielectric withstand voltage tests shall not proceed until insulation-resistance levels are raised above minimum values.

  - Results of SF6 gas tests shall be in accordance with Table 100.13.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand voltage test, the test specimen is considered to have passed the test.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the test specimen is considered to have passed the test.

  - Results of open and close operation from control devices shall be in accordance with system design.

  - Investigate fuse resistance values that deviate from each other by more than 15 percent.