# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.2	Circuit Breakers, Oil, Medium- and High-Voltage

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, grounding, and required clearances.

  - Verify that all maintenance devices such as special tools and gauges specified by the manufacturer are available for servicing and operating the breaker.

  - Verify correct oil level in all tanks and bushings.

  - Verify that breather vents are clear.

  - Verify the unit is clean.

  - Inspect hydraulic system and air compressor in accordance with manufacturer’s published data.

  - Test alarms and pressure-limit switches for pneumatic and hydraulic operators as recommended by the manufacturer.

  - Perform mechanical operation tests on the operating mechanism in accordance with manufacturer’s published data.

  - While performing internal inspection:

    - Remove oil. Lower tanks or remove manhole covers as necessary. Inspect bottom of tank for broken parts and debris.

    - Inspect lift rod and toggle assemblies, contacts, interrupters, bumpers, dashpots, bushing current transformers, tank liners, and gaskets.

    - Verify that contact sequence is in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use IEEE C37.04.

    - Fill tank(s) with filtered oil.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.6.2	Circuit Breakers, Oil, Medium- and High-Voltage (continued)

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.6.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

- Verify racking mechanism operation.

- Perform contact-timing test.

- Perform mechanism-motion analysis.

*17.	Perform trip/close coil current signature analysis.

- Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

- Record as-found and as-left operation counter readings.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.6.2.A.12.1

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with circuit-breaker closed, and across each open pole. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a static contact/pole resistance test.

*4.	Perform a dynamic contact/pole resistance test.

*5.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.6.2  Circuit Breakers, Oil, Medium- and High-Voltage (continued)

      - Remove a sample of insulating liquid in accordance with ASTM D 923. Sample shall be tested in accordance with the referenced standard.

        - Dielectric breakdown voltage: ASTM D 877

        - Color: ASTM D 1500

        - Power factor: ASTM D 924

        - Interfacial tension: ASTM D 971

        - Visual condition: ASTM D 1524

        - Neutralization number (acidity): ASTM D974

        - Water content: ASTM D1533

      - Perform minimum pickup voltage tests on trip and close coils in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.20.

      - Verify correct operation of any auxiliary features such as electrical close and trip operation, trip-free, antipump function.

      - Trip circuit breaker by operation of each protective device. Reset all trip logs and indicators.

      - Perform power-factor or dissipation-factor tests on each pole with breaker open and each phase with breaker closed. Determine tank loss index.

      - Perform power-factor or dissipation-factor tests on each bushing equipped with a power- factor/capacitance tap. In the absence of a power-factor/capacitance tap, perform hot-collar tests. These tests shall be in accordance with the test equipment manufacturer’s published data.

*12.	Perform a dielectric withstand voltage test in accordance with manufacturer’s published data.

- Verify operation of heaters.

- Test instrument transformers in accordance with Section 7.10.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.2	Circuit Breakers, Oil, Medium- and High-Voltage (continued)

## Test Values – Visual and Mechanical

  - Settings for alarm, pressure, and limit switches shall be in accordance with owner’s specifications. In the absence of owner’s specifications use manufacturer’s published data. (7.6.2.A.9).

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.6.2.A.12.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.6.2.A.12.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.6.2.A.12.3)

  - Contact timing values shall be in accordance with manufacturer’s published data. (7.6.2.A.15).

  - Travel and velocity values shall be in accordance with manufacturer’s published data. (7.6.2.A.16)

  - Trip/close coil current values shall be in accordance with manufacturer’s published data. (7.6.2.A.17).

  - Operations counter shall advance one digit per close-open cycle. (7.6.2.A.19)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values of circuit breakers shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. If manufacturer’s published data is not available, investigate values that deviate from adjacent poles or similar breakers by more than 50 percent of the lowest value.

  - Dynamic contact resistance values shall be in accordance with manufacturer’s published data.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.2	Circuit Breakers, Oil, Medium- and High-Voltage (continued)

  - Insulating liquid test results shall be in accordance with Table 100.4.

  - Minimum pickup voltage of the trip and close coils shall conform to the manufacturer’s published data. In the absence of the manufacturer’s published data, use Table 100.20.

  - Auxiliary features shall operate in accordance with manufacturer’s published data.

  - Protective devices shall operate the breaker per system design.

  - Power-factor or dissipation-factor values and tank loss index shall be compared to manufacturer’s published data. In the absence of manufacturer’s data, the comparison shall be made to test data from similar breakers or data from test equipment manufacturers.

  - Power-factor or dissipation-factor and capacitance values shall be within ten percent of nameplate rating for bushings. Hot collar tests are evaluated on a milliampere/milliwatt loss basis, and the results should be compared to values of similar bushings.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the test specimen is considered to have passed the test.

  - Heaters shall be operational.

  - Results of electrical tests on instrument transformers shall be in accordance with Section 7.10.