# 7.       INSPECTION AND TEST PROCEDURES

# 7.6.4	Circuit Breakers, SF6

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify that all maintenance devices such as special tools and gauges specified by the manufacturer are available for servicing and operating the breaker.

  - Verify the unit is clean.

  - When provisions are made for sampling, remove a sample of SF6 gas and test in accordance with Table 100.13. Do not break seal or distort “sealed-for-life” interrupters.

  - Inspect operating mechanism and/or hydraulic or pneumatic system and SF6 gas-insulated system in accordance with manufacturer’s published data.

  - Test for SF6 gas leaks in accordance with manufacturer’s published data.

  - Verify correct operation of alarms and pressure-limit switches for pneumatic, hydraulic, and SF6 gas pressure in accordance with manufacturer’s published data.

  - If recommended by manufacturer, slow close/open breaker and check for binding, friction, contact alignment, and penetration. Verify that contact sequence is in accordance with manufacturer’s published data. In the absence of manufacturer’s data, refer to IEEE C37.04.

  - Perform all mechanical operation tests on the operating mechanism in accordance with the manufacturer’s published data.

  - Inspect all bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.6.4.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform a thermographic survey in accordance with Section 9.

  - Verify the appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

7.       INSPECTION AND TEST PROCEDURES

7.6.4	Circuit Breakers, SF6 (continued)

  - Perform contact-timing test.

*15.	Perform trip/close coil signature analysis.

- Perform mechanism motion analysis.

- Record as-found and as-left operation counter readings.

## Electrical Tests

  - Perform resistance measurements through all bolted connections with a low-resistance ohmmeter in accordance with Section 7.6.4.A.12.1.

  - Perform insulation-resistance tests in accordance with Table 100.1 from each pole-to- ground with breaker closed and across open poles at each phase. For single-tank breakers, perform insulation resistance tests in accordance with Table 100.1 from pole-to-pole.

  - Perform a contact/pole-resistance test.

*4.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components or for control devices that cannot tolerate the voltage, follow manufacturer’s recommendation.

- Perform minimum pickup voltage tests on trip and close coils in accordance with manufacturer’s published data.

- Verify correct operation of any auxiliary features such as electrical close and trip operation, trip-free, and antipump function. Reset all trip logs and indicators.

- Trip circuit breaker by operation of each protective device.

- Perform power-factor or dissipation-factor tests on each pole with the breaker open and on each phase with the breaker closed.

- Perform power-factor or dissipation-factor tests on each bushing equipped with a power- factor/capacitance tap. In the absence of a power-factor/capacitance tap, perform hot-collar tests. These tests shall be in accordance with the test equipment manufacturer’s published data.

*10.	Perform a dielectric withstand voltage test in accordance with manufacturer’s published data.

- Verify operation of heaters.

- Test instrument transformers in accordance with Section 7.10.

7.      INSPECTION AND TEST PROCEDURES

7.6.4	Circuit Breakers, SF6 (continued)

## Test Values – Visual and Mechanical

  - SF6 gas shall have values in accordance with Table 100.13. (7.6.4.A.6)

  - Results of the SF6 gas leak test shall confirm that no SF6 gas leak exists. (7.6.4.A.8)

  - Settings for alarm, pressure, and limit switches shall be in accordance with manufacturer’s published data. (7.6.4.A.9)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.6.4.A.12.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.6.4.A.12.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.6.4.A.12.3)

  - Contact timing values shall be in accordance with manufacturer’s published data. (7.6.4.A.14)

  - Trip/close coil current values shall be in accordance with manufacturer’s published data. (7.6.4.A.15)

  - Travel and velocity values shall be in accordance with manufacturer’s published data. (7.6.4.A.16)

  - Operations counter shall advance one digit per close-open cycle. (7.6.4.A.17)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values of circuit breakers shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. In the absence of manufacturer’s data, investigate values that deviate from adjacent poles or similar breakers by more than 50 percent of the lowest value.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

7.       INSPECTION AND TEST PROCEDURES

7.6.4	Circuit Breakers, SF6 (continued)

  - Minimum pickup voltage of the trip and close coils shall conform to the manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.20.

  - Auxiliary features shall operate in accordance with manufacturer’s published data.

  - Protective devices shall operate the breaker per the system design.

  - Power-factor or dissipation-factor values shall be compared to manufacturer’s published data. In the absence of manufacturer’s data, the comparison shall be made to test data from similar breakers or data from test equipment manufacturers.

  - Power-factor or dissipation-factor and capacitance test values shall be within ten percent of nameplate rating for bushings. Hot collar tests are evaluated on a milliampere/milliwatt loss basis, and the results shall be compared to values of similar bushings.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the test specimen is considered to have passed the test.

  - Heaters shall be operational.

  - Results of electrical tests on instrument transformers shall be in accordance with Section 7.10.