# 7.        INSPECTION AND TEST PROCEDURES

# 7.7	Circuit Switchers

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the bushings and insulators are clean.

  - Verify both the circuit switcher and its operating mechanism mechanically operate in accordance with the manufacturer’s published data.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.7.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify operation of SF6 interrupters is in accordance with manufacturer’s published data.

  - Verify SF6 pressure is in accordance with manufacturer’s published data.

  - Verify operation of isolating switch is in accordance with system design and manufacturer’s published data.

  - Verify all interlocking systems operate and sequence per system design and manufacturer’s published data.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

  - Record as-found and as-left operation counter readings.

## B	Electrical Tests

- Perform resistance measurements through all connections with a low-resistance ohmmeter in accordance with Section 7.7.A.6.

- Perform contact-resistance test of interrupters and isolating switches.

7.        INSPECTION AND TEST PROCEDURES

7.7	Circuit Switchers (continued)

- Perform insulation-resistance tests on each pole phase-to-ground. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

*4.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

- Perform minimum pickup voltage tests on trip and close-coils in accordance with manufacturer’s published data.

- Verify correct operation of any auxiliary features such as electrical close and trip operation, trip-free, and anti-pump function. Reset all trip logs and indicators.

- Trip circuit switcher by operation of each protective device.

- Verify correct operation of electrical trip of interrupters.

- Perform a dielectric withstand voltage test in accordance with the manufacturer’s published data.

- Verify operation of heaters.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.7.A.6.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.7.A.6.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.7.A.6.3)

  - SF6 interrupters shall operate in accordance with manufacturer’s published data. (7.7.A.7)

  - SF6 pressure shall be in accordance with manufacturer’s published data. (7.7.A.8)

  - Isolating switch shall operate in accordance with system and manufacturer’s design. (7.7.A.9)

  - Interlocking systems shall operate in accordance with system and manufacturer’s design. (7.7.A.10)

  - Operation counter shall advance one digit per close-open cycle. (7.7.A.12)

7.        INSPECTION AND TEST PROCEDURES

7.7	Circuit Switchers (continued)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. In the absence of manufacturer’s data, investigate values that deviate from adjacent poles or similar breakers by more than 50 percent of the lowest value.

  - Insulation-resistance values of circuit switchers shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - Minimum pickup voltage of the trip and close coils shall conform to the manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.20.

  - Auxiliary features shall operate in accordance with manufacturer’s published data.

  - Protective devices shall operate the circuit switcher in accordance with the system design.

  - Electrical trip interrupters shall function as designed.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the circuit switcher is considered to have passed the test.

  - Heaters shall be operational.