# INSPECTION AND TEST PROCEDURES

# Switchgear and Switchboard Assemblies

# Visual and Mechanical Inspections

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical, electrical, and mechanical condition of cords and connectors.

  - Inspect anchorage, alignment, grounding, and required area clearances.

  - Verify the unit is clean and all shipping bracing, loose parts, and documentation shipped inside cubicles have been removed.

  - Verify that fuse and circuit breaker sizes and types correspond to drawings and coordination study as well as to the circuit breaker address for microprocessor-communication packages.

  - Verify that current and voltage transformer ratios correspond to drawings.

  - Verify that wiring connections are tight and that wiring is secure to prevent damage during routine operation of moving parts.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.1.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Confirm correct operation and sequencing of electrical and mechanical interlock systems.

    - Attempt closure on locked-open devices. Attempt to open locked-closed devices.

    - Make key exchange with all devices included in the interlock scheme.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

  - Inspect insulators for evidence of physical damage or contaminated surfaces.

  - Verify correct barrier and shutter installation and operation.

Page 24

ANSI/NETA ATS-2021

  - Exercise all active components.

  - Inspect mechanical indicating devices for correct operation.

  - Verify that filters are in place and vents are clear.

  - Perform visual and mechanical inspection of instrument transformers in accordance with Section 7.10.

  - Perform visual and mechanical inspection of surge arresters in accordance with Section 7.19.

  - Inspect control power transformers.

    - Inspect for physical damage, cracked insulation, broken leads, tightness of connections, defective wiring, and overall general condition.

    - Verify that primary and secondary fuse or circuit breaker ratings match drawings.

    - Verify correct functioning of drawout disconnecting contacts, grounding contacts, and interlocks.

# Electrical Tests

  - Perform resistance measurements through bolted electrical connections with a low- resistance ohmmeter in accordance with Section 7.1.A.8.1.

  - Perform insulation-resistance tests for one minute on each bus section, phase-to-phase and phase-to-ground. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a dielectric withstand voltage test on each bus section, each phase-to-ground with phases not under test grounded, in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.2. The test voltage shall be applied for one minute. Refer to Section 7.13 before performing tests.

*4.	Perform insulation-resistance tests on control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components or control devices that cannot tolerate the applied voltage, follow the manufacturer’s recommendation.

- Perform electrical tests on instrument transformers in accordance with Section 7.10.

- Perform ground-resistance tests in accordance with Section 7.13.

- Test metering devices in accordance with Section 7.11.

- Control Power Transformers

  - Perform insulation-resistance tests. Perform measurements from winding-to-winding and each winding-to-ground. Test voltages shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a turns-ratio test on all tap positions.

  - Perform secondary wiring integrity test. Disconnect transformer at secondary terminals and connect secondary wiring to a rated secondary voltage source. Verify correct potential at all devices.

  - Verify correct secondary voltage by energizing the primary winding with system voltage. Measure secondary voltage with the secondary wiring disconnected.

  - Verify correct function of control transfer relays located in the switchgear with multiple control power sources.

- Voltage Transformers

  - Perform secondary wiring integrity test. Verify correct potential at all devices.

  - Verify secondary voltages by energizing the primary winding with system voltage.

- Perform current-injection tests on the entire current circuit in each section of switchgear.

  - Perform current tests by secondary injection with magnitudes such that a minimum current of 1.0 ampere flows in the secondary circuit. Verify correct magnitude of current at each device in the circuit.

*2.	Perform current tests by primary injection with magnitudes such that a minimum of

1.0 ampere flows in the secondary circuit. Verify correct magnitude of current at each device in the circuit.

- Perform system function tests in accordance with ANSI/NETA ECS Standard for Electrical Commissioning Specifications for Electrical Power Equipment and Systems.

- Verify operation of cubicle switchgear/switchboard space heaters and their controller.

- Perform phasing checks on double-ended or dual-source switchgear to insure correct bus phasing from each source.

- Perform electrical tests of surge arresters in accordance with Section 7.19.

*15.	Perform online partial-discharge survey in accordance with Section 11.

# Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.1.A.8.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.1.A.8.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.1.A.8.3)

# Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values of bus insulation shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. Dielectric withstand voltage tests shall not proceed until insulation-resistance levels are raised above minimum values.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the test specimen is considered to have passed the test.

  - Minimum insulation resistance values of control wiring shall not be less than two megohms.

  - Results of electrical tests on instrument transformers shall be in accordance with Section 7.10.

  - Results of ground resistance tests shall be in accordance with Section 7.13.

  - Accuracy of metering devices shall be in accordance with Section 7.11.

  - Control Power Transformers

    - Insulation-resistance values of control power transformers shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table

100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

    - Turns-ratio test results shall not deviate by more than one-half percent from either the adjacent coils or the calculated ratio.

    - Secondary wiring shall be in accordance with design drawings and specifications.

    - Secondary voltage shall be in accordance with design specifications.

    - Control transfer relays shall perform as designed.

  - Voltage transformers

    - Secondary wiring shall be in accordance with design drawings and specifications.

    - Secondary voltage shall be in accordance with design specifications

  - Current-injection tests shall prove current wiring is in accordance with design specifications.

  - Results of system function tests shall be in accordance with ANSI/NETA ECS.

  - Heaters shall be operational.

  - Phasing checks shall prove the switchgear or switchboard phasing is correct and in accordance with the system design.

  - Results of electrical tests on surge arresters shall be in accordance with Section 7.19.

  - Results of online partial-discharge survey should be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, refer to Table 100.23.