# 7.       INSPECTION AND TEST PROCEDURES

# 7.10.1	Instrument Transformers, Current Transformer

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Verify correct connection of transformers with system requirements.

  - Verify that adequate clearances exist between primary and secondary circuit wiring.

  - Verify the unit is clean.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.10.1.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify that all required grounding and shorting connections provide contact.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

## Electrical Tests – Current Transformers

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.10.1.A.6.1.

  - Perform insulation-resistance test of each current transformer and its secondary wiring with respect to ground at 1000 volts dc for one minute. For units with solid-state components that cannot tolerate the applied voltage, follow manufacturer’s recommendations.

  - Perform a polarity test of each current transformer in accordance with IEEE C57.13.1.

  - Perform a ratio-verification test using the voltage or current method in accordance with IEEE C57.13.1.

  - Perform an excitation test on transformers used for relaying applications in accordance with IEEE C57.13.1.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.10.1	Instrument Transformers, Current Transformer (continued)

  - Measure current circuit burdens at CT shorting terminal block in accordance with IEEE C57.13.1

  - Perform insulation-resistance tests on the primary winding with the secondary grounded. Test voltages shall be in accordance with Table 100.5.

*8.	Perform dielectric withstand tests on the primary winding with the secondary grounded.

Test voltages shall be in accordance with Table 100.9.

- Perform power-factor or dissipation-factor tests in accordance with manufacturer’s published data.

- Verify that current transformer secondary circuits are grounded and have only one grounding point in accordance with IEEE C57.13.3. That grounding point should be located as specified by the engineer in the project drawings.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.10.1.A.6.1)

  - Bolt torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.10.1.A.6.2)

  - Results of the thermographic survey shall be in accordance with Section 9.	(7.10.1.A.6.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values of instrument transformers shall not be less than values shown in Table 100.5.

  - Polarity results shall agree with transformer markings.

  - Ratio errors shall be in accordance with IEEE C57.13.

  - Excitation results shall match the curve supplied by the manufacturer or be in accordance with IEEE C57.13.1.

  - Compare measured burdens to instrument transformer ratings.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.10.1	Instrument Transformers, Current Transformer (continued)

  - Insulation-resistance values of instrument transformers shall not be less than values shown in Table 100.5.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the primary winding is considered to have passed the test.

  - Power-factor or dissipation-factor values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use test equipment manufacturer’s published data.

  - Test results shall indicate that the circuits have only one grounding point.