# 7.       INSPECTION AND TEST PROCEDURES

# 7.10.2	Instrument Transformers, Voltage Transformers

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Verify correct connection of transformers with system requirements.

  - Verify that adequate clearances exist between primary and secondary circuit wiring.

  - Verify the unit is clean.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods.

    - Use of low-resistance ohmmeter in accordance with Section 7.10.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify that all required grounding and connections provide contact.

  - Verify correct primary and secondary fuse sizes for voltage transformers.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

  - Perform as-left tests.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.10.2.A.6.1.

  - Perform insulation-resistance tests for one minute winding-to-winding and each winding-to- ground. Test voltages shall be applied for one minute in accordance with Table 100.5. For units with solid-state components that cannot tolerate the applied voltage, follow manufacturer’s recommendations.

  - Perform a polarity test on each transformer to verify the polarity marks or H1-X1 relationship as applicable.

  - Perform a turns-ratio test on all tap positions.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.10.2	Instrument Transformers, Voltage Transformers (continued)

  - Measure voltage circuit burdens at transformer terminals.

*6. Perform a dielectric withstand test on the primary windings with the secondary windings connected to ground. The dielectric voltage shall be in accordance with Table 100.9. The test voltage shall be applied for one minute.

- Perform power-factor or dissipation-factor tests in accordance with manufacturer’s published data.

- Verify that voltage transformer secondary circuits are grounded and have only one grounding point in accordance with IEEE C57.13.3. The grounding point should be located as specified by the engineer in the project drawings.

## C	Test Values – Visual and Mechanical

- Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.10.2.A.6.1)

- Bolt torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.10.2.A.6.2)

- Results of the thermographic survey shall be in accordance with Section 9. (7.10.2.A.6.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values of instrument transformers shall not be less than values shown in Table 100.5.

  - Polarity results shall agree with transformer markings.

  - In accordance with IEEE C57.13.8.1.1, the ratio error shall be as follows:

    - Revenue metering applications: equal to or less than ±0.1 percent for ratio and ±0.9 mrad (three minutes) for phase angle.

    - Other applications: equal to or less than +1.2 percent for ratio and ±17.5 mrad (one degree) for phase angle.

  - Compare measured burdens to instrument transformer ratings.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.10.2	Instrument Transformers, Voltage Transformers (continued)

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the primary windings are considered to have passed the test.

  - Power-factor or dissipation-factor values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use test equipment manufacturer’s published data.

  - Test results shall indicate that the circuits are grounded at only one point.