# 7.        INSPECTION AND TEST PROCEDURES

# 7.12.1.1	Regulating Apparatus, Voltage, Step Voltage Regulators

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect impact recorder prior to unloading regulator.

  - Inspect anchorage, alignment, and grounding.

  - Verify removal of any shipping bracing and vent plugs after final placement.

  - Verify the unit is clean.

  - Verify auxiliary device operation.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.12.1.1.B.1.

    - Verify tightness of accessible-bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify correct operation of motor and drive train and automatic motor cutoff at maximum lower and raise positions.

  - Verify appropriate lubrication on drive motor components.

  - Verify correct liquid level in all tanks and bushings.

  - Perform specific inspections and mechanical tests as recommended by the manufacturer.

  - Record as-found and as-left operation counter readings.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.12.1.1.A.8.1.

  - Perform insulation-resistance tests on each winding-to-ground in any off-neutral position. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.5. Calculate polarization index.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.12.1.1	Regulating Apparatus, Voltage, Step Voltage Regulators (continued)

  - Perform insulation power-factor or dissipation-factor tests on windings in accordance with test equipment manufacturer’s published data.

  - Perform power-factor or dissipation-factor tests on each bushing equipped with a power- factor/ capacitance tap. In the absence of a power-factor/ capacitance tap, perform hot-collar tests. These tests shall be in accordance with the test equipment manufacturer’s published data.

  - Measure winding resistance of source windings in the neutral position. Measure the resistance of all taps on load windings.

  - Perform special tests and adjustments as recommended by manufacturer.

*7.	If the regulator has a separate tap-changer compartment, test for the presence of oxygen in the gas blanket in the main tank.

- Perform turns-ratio test on each voltage step position. Verify that the indicator correctly identifies all tap positions.

- Verify accurate operation of voltage range limiter.

- Verify operation and accuracy of bandwidth, time delay, voltage, and line-drop compensation functions of regulator control device.

- Sample insulating liquid in the main tank and tap-changer tank or common tank in accordance with ASTM D923 and perform dissolved-gas analysis in accordance with IEEE C57.104 or ASTM D 3612.

- Remove a sample of insulating liquid from the main tank or common tank in accordance with ASTM D 923. Sample shall be tested in accordance with the referenced standard.

  - Dielectric breakdown voltage: ASTM D 877 and/or ASTM D 1816

  - Acid neutralization number: ASTM D 974

  - Specific gravity: ASTM D 1298

  - Interfacial tension: ASTM D 971

  - Color: ASTM D 1500

  - Visual condition: ASTM D 1524

*7.	Power factor: ASTM D 924

Required when the regulator voltage is 46 kV or higher.

8.	Water in insulating liquids: ASTM D 1533

# 7.        INSPECTION AND TEST PROCEDURES

# 7.12.1.1	Regulating Apparatus, Voltage, Step Voltage Regulators (continued)

- If the regulator has a separate tap-changer compartment remove a sample of insulating liquid from the tap-changer tank in accordance with ASTM D 923. Sample shall be tested in accordance with the referenced standard.

  - Dielectric breakdown voltage: ASTM D 877

  - Color: ASTM D 1500

  - Visual condition: ASTM D 1524

- Verify operation of heaters.

## Test Values – Visual and Mechanical

  - Auxiliary devices should operate in accordance with system design. (7.12.1.1.A.7)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.12.1.1.A.8.1)

  - Bolt-torque levels should be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.12.1.1.A.8.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.12.1.1.A.8.3)

  - Motor, drive train, and automatic cutoff should operate in accordance with manufacturer’s design. (7.12.1.1.A.9)

  - Liquid level in tanks and bushings should be within indicated tolerances. (7.12.1.1.A.10)

  - The operation counter shall move incrementally for each operation performed. (7.12.1.1.A.13)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.12.1.1	Regulating Apparatus, Voltage, Step Voltage Regulators (continued)

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.5. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. Resistance values shall be temperature corrected in accordance with Table 100.14. The polarization index shall be compared to manufacturer’s factory test results. If manufacturer’s test results are not available the polarization index value shall not be less than 1.0.

  - Maximum power-factor or dissipation-factor values of liquid-filled regulators shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, compare to test equipment manufacturer’s published data. Representative-values are indicated in Table 100.3.

  - Power-factor or dissipation-factor and capacitance values shall be within ten percent of nameplate rating for bushings. Hot collar tests are evaluated on a milliampere/milliwatt loss basis, and the results shall be compared to values of similar bushings.

  - Consult the manufacturer if winding-resistance test values vary by more than two percent from factory test values or between adjacent phases.

  - Special tests and adjustments shall meet manufacturer’s published requirements.

  - Investigate presence of oxygen in nitrogen gas blanket.

  - Turns-ratio test results shall maintain a normal deviation between each voltage step and shall not deviate more than one-half percent from the calculated voltage ratio.

  - Voltage range limiter shall operate within manufacturer’s recommendations.

  - Operation and accuracy of bandwidth, time-delay, voltage, and live drop compensation functions shall be as specified.

  - Results of dissolved gas analysis shall be evaluated in accordance with IEEE C57.104 or ASTM D 3612.

  - Results of insulating liquid tests on the main tank of regulators having a separate tap- changer compartment or the common tank of single tank voltage regulators shall be in accordance with Table 100.4.

  - Results of insulating liquid tests on the tap-changer tank of regulators having a separate tap- changer compartment shall be in accordance with Table 100.4.

  - Heaters shall be operational.