# 7.        INSPECTION AND TEST PROCEDURES

# 7.12.3	Regulating Apparatus, Load Tap-Changers

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Inspect impact recorder.

  - Verify removal of any shipping bracing and vent plugs.

  - Verify the unit is clean.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.12.3.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify correct auxiliary device operation.

  - Verify correct operation of motor and drive train and automatic motor cutoff at maximum lower and maximum raise positions.

  - Verify appropriate liquid level in all tanks.

  - Perform specific inspections and mechanical tests as recommended by the manufacturer.

  - Verify appropriate lubrication on motor components.

  - Record as-found and as-left operation counter readings.

## Electrical Tests

  - Perform resistance measurements through bolted connections with low-resistance ohmmeter in accordance with Section 7.12.3.A.7.1.

  - Perform insulation-resistance tests in any off-neutral position in accordance with Section 7.2.2.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.12.3	Regulating Apparatus, Load Tap-Changers (continued)

  - Perform insulation power-factor or dissipation-factor tests in accordance with Section 7.2.2.

*4.	Perform winding-resistance test at each tap position.

- Perform special tests and adjustments as recommended by the manufacturer.

- Perform turns-ratio test at all tap positions.

- Remove a sample of insulating liquid in accordance with ASTM D 923. The sample shall be tested for the following in accordance with the referenced standard.

  - Dielectric breakdown voltage: ASTM D 877

  - Color: ASTM D 1500

  - Visual condition: ASTM D 1524

- Remove a sample of insulating liquid in accordance with ASTM D923 and perform dissolved gas analysis in accordance with IEEE C57.104 or ASTM D 3612.

*9	Perform magnetron atmospheric condition (MAC) test on each vacuum interrupter.

*10.	Perform vacuum bottle integrity tests (dielectric withstand voltage) across each vacuum bottle with the contacts in the open position in strict accordance with manufacturer’s published data.

11.	Verify operation of heaters.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.12.3.A.7.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.12.3.A.7.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.12.3.A.7.3)

  - Auxiliary device operation shall be in accordance with design intent. (7.12.3.A.8)

  - Motor, drive train, and automatic cutoff shall operate in accordance with manufacturer’s design intent and automatic motor cutoff shall operate at maximum lower and maximum raise positions. (7.12.3.A.9)

  - Liquid level in tanks shall be within indicated tolerances. (7.12.3.A.10)

# 7.        INSPECTION AND TEST PROCEDURES

# 7.12.3	Regulating Apparatus, Load Tap-Changers (continued)

  - Operation counter shall have had an incremental change in accordance with tap-changer operation. (7.12.3.A.13)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.5. Values of insulation resistance less than this table or manufacturer’s recommendations shall be investigated.

  - Maximum winding insulation power-factor/dissipation-factor values of liquid-filled transformers shall be in accordance with the transformer manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.3.

  - Consult the manufacturer if winding-resistance values vary by more than one percent from measurements of adjacent windings.

  - Special tests and adjustments shall be in accordance with manufacturer’s published data.

  - Turns-ratio test results shall maintain a normal deviation between each voltage step and shall not deviate more than one-half percent from the calculated voltage ratio.

  - Results of insulating liquid tests shall be in accordance with Table 100.4.

  - Results of dissolved-gas analysis shall be evaluated in accordance with IEEE C57.104.

  - In the absence of manufacturer’s published data, each vacuum interrupter pressure shall not be greater than 1x10-2 Pa and shall not deviate from adjacent poles by more than two orders of magnitude.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the test specimen is considered to have passed the test.

  - Heaters shall be operational.