# 7.       INSPECTION AND TEST PROCEDURES

# 7.16.1.1	Motor Control, Motor Starters, Low-Voltage

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

  - Inspect contactors.

    - Verify mechanical operation.

    - Verify contact gap, wipe, alignment, and pressure are in accordance with manufacturer’s published data.

*6.	Motor-Running Protection

- Verify overload element rating/motor protection settings are correct for application.

- If motor-running protection is provided by fuses, verify correct fuse rating.

- Inspect bolted electrical connections for high resistance using one or more of the following methods:

  - Use of low-resistance ohmmeter in accordance with Section 7.16.1.1.B.1.

  - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

  - Perform thermographic survey in accordance with Section 9.

- Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.16.1.1.A.7.1.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with starter closed, and across each open pole. Test voltage shall be in accordance with manufacturer’s published data or Table 100.1.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.16.1.1	Motor Control, Motor Starters, Low-Voltage (continued)

*3.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

- Test motor protection devices in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Section 7.9.

- Test circuit breakers in accordance with Section 7.6.1.1.

- Perform operational al tests by initiating control devices.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.16.1.1.A.7.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.16.1.1.A.7.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.16.1.1.A.7.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations shall be investigated.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - Motor protection parameters shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Section 7.9.

  - Circuit breaker test results shall be in accordance with Section 7.6.1.1.

  - Control devices shall perform in accordance with system design and/or requirements.