# 7.       INSPECTION AND TEST PROCEDURES

# 7.17	Adjustable Speed Drive Systems

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

  - Ensure vent path openings are free from debris and that heat transfer surfaces are not contaminated by oil, dust, and dirt.

  - Verify correct connections of circuit boards, wiring, disconnects, and ribbon cables.

  - Motor running protection

    - Compare drive overcurrent setpoints with motor full-load current rating to verify correct settings.

    - If drive is used to operate multiple motors, compare individual overload element ratings with motor full-load current ratings.

    - Apply minimum and maximum speed setpoints. Confirm setpoints are within limitations of the load coupled to the motor.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.17.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify correct fuse sizing in accordance with manufacturer’s published data.

## Electrical Tests

  - Perform resistance measurements through bolted connections with low-resistance ohmmeter in accordance with Section 7.17.A.8.1.

  - Test the motor overload relay elements by injecting primary current through the overload circuit and monitoring trip time of the overload element.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.17	Adjustable Speed Drive Systems (continued)

  - Test input circuit breaker by primary injection in accordance with Section 7.6.

*4.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

- Test for the following parameters in accordance with relay calibration procedures outlined in Section 7.9 or as recommended by the manufacturer:

  - Input phase loss protection

  - Input overvoltage protection

  - Output phase rotation

  - Overtemperature protection

  - DC overvoltage protection

  - Overfrequency protection

  - Drive overload protection

  - Fault alarm outputs

- Perform continuity tests on bonding conductors in accordance with Section 7.13.

- Perform startup of drive in accordance with manufacturer’s published data. Calibrate drive to the system’s minimum and maximum speed control signals.

- Perform operational tests by initiating control devices.

  - Slowly vary drive speed between minimum and maximum. Observe motor and load for unusual noise or vibration.

  - Verify operation of drive from remote start/stop and speed control signals.

- Measure fuse resistance.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.17	Adjustable Speed Drive Systems (continued)

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.17.A.8.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.17.A.8.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.17.A.8.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Overload test trip times at 300 percent of overload element rating shall be in accordance with manufacturer’s published time-current curve.

  - Input circuit breaker test results shall be in accordance with Section 7.6.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - Relay calibration test results shall be in accordance with Section 7.9.

  - Continuity of bonding conductors shall be in accordance with Section 7.13.

  - Control devices shall perform in accordance with system requirements.

  - Operational tests shall conform to system design requirements.

  - Investigate fuse resistance values that deviate from each other by more than 15 percent.