# 7.       INSPECTION AND TEST PROCEDURES

# 7.18.2	Direct-Current Systems, Chargers

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect for physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

  - Inspect all bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.18.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey under load in accordance with Section 9.

  - Inspect filter and tank capacitors.

  - Verify operation of cooling fans and presence of filters.

## Electrical Tests

  - Perform resistance measurements through all bolted connections with a low-resistance ohmmeter in accordance with Section 7.18.2.A.5.1.

  - Verify float voltage and equalize voltage.

  - Verify high-voltage shutdown settings.

  - Verify correct load sharing (parallel chargers).

  - Verify calibration of meters in accordance with Section 7.11.

  - Verify operation of alarms.

  - Measure and record input and output voltage and current.

  - Measure and record ac ripple current and voltage imposed on the battery.

*9.	Perform full load testing and verify current limit of charger.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.18.2	Direct-Current Systems, Chargers (continued)

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.18.2.A.5.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.18.2.A.5.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.18.2.A.5.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values that deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Float and equalize voltage settings shall be in accordance with the manufacturer’s published data.

  - High- voltage shutdown settings shall be in accordance with manufactuer’s published data.

  - Results of load sharing between parallel chargers shall be in accordance with system design specifications.

  - Results of meter calibration shall be in accordance with Section 7.11.

  - Results of alarm operation shall be in accordance with manufacturer’s published data and system design.

  - Input and output voltage shall be in accordance with manufacturer’s published data.

  - AC ripple current and voltage imposed on the battery shall be in accordance with manufacturer’s published data.

  - Charger shall be capable of producing rated full load output and current limit shall be in accordance with the specified settings.