# 7.       INSPECTION AND TEST PROCEDURES

# 7.20.3.1		Capacitors and Reactors, Reactors (Shunt and Current-Limiting) Dry- Type

## Visual and Mechanical Inspections

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.20.3.1.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify that tap connections are as specified.

## Electrical Tests

  - Perform resistance measurements through bolted connections with low-resistance ohmmeter in accordance with Section 7.20.3.1.A.5.1.

  - Perform winding-to-ground insulation-resistance tests. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, refer to Table 100.1.

  - Measure winding resistance.

*4.	Perform dielectric withstand voltage tests on each winding to ground.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.20.3.1.A.5.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.20.3.1.A.5.2)

# 7.       INSPECTION AND TEST PROCEDURES

# 7.20.3.1		Capacitors and Reactors, Reactors (Shunt and Current-Limiting) Dry- Type (continued)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.20.3.1.A.5.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Winding-resistance test results shall be within one percent of factory results.

  - AC dielectric withstand test voltage shall not exceed 75 percent of factory test voltage for one minute duration. DC dielectric withstand test voltage shall not exceed 100 percent of the factory rms test voltage for one minute duration. If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the test specimen is considered to have passed the test.