# 7.       INSPECTION AND TEST PROCEDURES

# 7.20.3.2		Capacitors and Reactors, Reactors (Shunt and Current-Limiting) Liquid- Filled

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect impact recorder prior to unloading.

  - Verify removal of any shipping bracing after final placement.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

  - Verify settings and operation of all temperature devices.

  - Verify that cooling fans and pumps operate correctly and that fan and pump motors have correct overcurrent protection.

  - Verify operation of all alarm, control, and trip circuits from temperature and level indicators, pressure relief device, and fault pressure relay.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.20.3.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify correct liquid level in all tanks and bushings.

  - Verify that positive pressure is maintained on nitrogen-blanketed reactors.

  - Perform specific inspections and mechanical tests as recommended by the manufacturer.

  - Verify that tap connections are as specified.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.20.3.2		Capacitors and Reactors, Reactors (Shunt and Current-Limiting) Liquid- Filled (continued)

## Electrical Tests

  - Perform resistance measurements through bolted connections with low-resistance ohmmeter in accordance with Section 7.20.3.2.A.10.1.

  - Perform winding-to-ground insulation-resistance tests. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Calculate polarization index.

  - Perform insulation power-factor or dissipation-factor tests on windings in accordance with the test equipment manufacturer’s published data.

  - Perform power-factor or dissipation-factor tests on each bushing equipped with a power- factor/ capacitance tap. In the absence of a power-factor/ capacitance tap, perform hot-collar tests. These tests shall be in accordance with the test equipment manufacturer’s published data.

  - Measure winding resistance.

  - Measure the percentage of oxygen in the nitrogen gas blanket.

  - Remove a sample of insulating liquid in accordance with ASTM D923. Sample shall be tested for the following:

    - Dielectric breakdown voltage: ASTM D1816.

    - Acid neutralization number: ASTM D974.

    - Specific gravity: ASTM D1298.

    - Interfacial tension: ASTM D971.

    - Color: ASTM D1500.

    - Visual Condition: ASTM D1524.

    - Water in insulating liquids: ASTM D1533.

*8.	Measure power factor or dissipation factor in accordance with ASTM D924.

  - Remove a sample of insulating liquid in accordance with ASTM D923and perform dissolved-gas analysis in accordance with IEEE C57.104 or ASTM D-3612.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.20.3.2		Capacitors and Reactors, Reactors (Shunt and Current-Limiting) Liquid- Filled (continued)

## Test Values – Visual and Mechanical

  - Operation of temperature devices shall be in accordance with system requirements. (7.20.3.2.A.7)

  - Operation of pumps and fans shall be in accordance with manufacturer’s recommendations and system design. (7.20.3.2.A.8)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.20.3.2.A.10.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.12. (7.20.3.2.A.10.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.20.3.2.A.10.3)

  - Liquid levels shall be in accordance with manufacturer’s published tolerances. (7.20.3.2.A.11)

  - Positive pressure shall be indicated on the pressure gauge for gas-blanketed reactors. (7.20.3.2.A.12)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. The polarization index shall be greater than 1.0.

  - Maximum power-factor or dissipation-factor values of liquid-filled reactors shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, compare to test equipment manufacturer’s published data. Representative values are indicated in Table 100.3.

  - Power-factor or dissipation-factor and capacitance values shall be within ten percent of nameplate rating for bushings. Hot collar tests are evaluated on a milliampere/ milliwatt-loss basis, and the results shall be compared to values of similar bushings.

  - Consult the manufacturer if winding-resistance test values vary by more than two percent from factory test values or between adjacent phases.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.20.3.2		Capacitors and Reactors, Reactors (Shunt and Current-Limiting) Liquid- Filled (continued)

  - Investigate presence of oxygen in the nitrogen gas blanket.

  - Insulating liquid values shall be in accordance with Table 100.4.

  - Results of dissolved-gas analysis shall be evaluated in accordance with IEEE Standard C57.104.