# 7.       INSPECTION AND TEST PROCEDURES

# 7.22.1	Emergency Systems, Engine Generator

NOTE: Other than protective shutdowns, the prime mover is not addressed in these specifications.

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

## Electrical and Mechanical Tests

  - Perform insulation-resistance tests in accordance with IEEE 43.

- Machines larger than 200 horsepower (150 kilowatts):

Test duration shall be ten minutes. Calculate polarization index.

- Machines 200 horsepower (150 kilowatts) and less:

Test duration shall be one minute. Calculate the dielectric-absorption ratio.

  - Test protective relay devices in accordance with Section 7.9.

  - Verify phase rotation, phasing, and synchronized operation as required by the application.

  - Functionally test engine shutdown for low oil pressure, overtemperature, overspeed, and other protection features as applicable.

*5.	Perform vibration test for each main bearing cap.

- Conduct performance test in accordance with NFPA 110.

- Verify correct functioning of the governor and regulator.

## Test Values – Visual and Mechanical

  - Anchorage, alignment, and grounding should be in accordance with manufacturer’s published data and system design. (7.22.1.A.3)

# 7.       INSPECTION AND TEST PROCEDURES

# 7.22.1	Emergency Systems, Engine Generator (continued)

## Test Values – Electrical

  - The recommended minimum insulation resistance (IR 1 min) test results in megohms shall be in accordance with Table 100.11.

    - The polarization index value shall not be less than 2.0.

    - The dielectric absorption ratio shall be greater than 1.0.

  - Protective relay device test results shall be in accordance with Section 7.9.

  - Phase rotation, phasing, and synchronizing shall be in accordance with system design requirements.

  - Low oil pressure, overtemperature, overspeed, and other protection features shall operate in accordance with manufacturer’s published data and system design requirements.

  - Vibration levels shall be in accordance with manufacturer’s published data and shall be compared to baseline data.

  - Performance tests shall conform to manufacturer’s published data and NFPA 110.

  - Governor and regulator shall operate in accordance with manufacturer’s published data and system design requirements.