# 7.         INSPECTION AND TEST PROCEDURES

# 7.24.1 Automatic Circuit Reclosers and Line Sectionalizers,

# Automatic Circuit Reclosers, Oil/Vacuum

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

  - Perform all mechanical operation and contact alignment tests on both the recloser and its operating mechanism in accordance with manufacturer’s published data.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.24.1.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify appropriate insulating liquid level.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.24.1.A.6.1.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with recloser closed, and across each open pole. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.1.

  - Perform a contact/pole-resistance test.

*4.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

- Remove a sample of insulating liquid in accordance with ASTM D 923. Sample shall be tested in accordance with the referenced standard.

  - Dielectric breakdown voltage: ASTM D 877

  - Color: ASTM D 1500

  - Visual condition: ASTM D 1524

- Perform minimum pickup voltage tests on trip and close coils in accordance with manufacturer’s published data.

*7.	Perform power-factor or dissipation-factor tests on each pole with the recloser open and each phase with the recloser closed.

*8.	Perform power-factor or dissipation-factor tests on each bushing equipped with a power- factor/capacitance tap. In the absence of a power-factor/capacitance tap, perform hot-collar tests. These tests shall be in accordance with the test equipment manufacturer’s published data.

*9.	Perform magnetron atmospheric condition (MAC) test on each vacuum interrupter.

- Perform vacuum bottle integrity test (dielectric withstand voltage) across each vacuum bottle with the contacts in the open position in strict accordance with manufacturer’s published data.

- Perform dielectric withstand voltage test on each phase with the recloser closed and the poles not under test grounded. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.19.

- Verify operation of heaters.

- Test all protective functions in accordance with Section 7.9.

- Test all metering and instrumentation in accordance with Section 7.11.

- Test instrument transformers in accordance with Section 7.10.

## Test Values – Visual and Mechanical

  - Mechanical operation and contact alignment shall be in accordance with manufacturer’s published data. (7.24.1.A.5)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.24.1.A.6.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.12. (7.24.1.A.6.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.24.1.A.6.3)

  - Insulating liquid level shall be in accordance with manufacturer’s recommended tolerances. (7.24.1.A.7)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations shall be investigated.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. If manufacturer’s published data is not available, investigate values that deviate from adjacent poles or similar reclosers by more than 50 percent of the lowest value.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - Insulating liquid test results shall be in accordance with Table 100.4.

  - Minimum pickup voltage of the trip and close coils shall conform to the manufacturer’s published data. In the absence of the manufacturer’s published data, use Table 100.20.

  - Power-factor or dissipation-factor values and tank loss-index shall be compared to manufacturer’s published data. In the absence of manufacturer’s published data, the comparison shall be made to test data from similar circuit reclosers or data from test equipment manufacturers.

  - Power-factor or dissipation-factor and capacitance values shall be within ten percent of nameplate rating for bushings. Hot collar tests are evaluated on a milliampere/milliwatt loss basis, and the results shall be compared to values of similar bushings.

  - In the absence of manufacturer’s published data, each vacuum interrupter pressure shall not be greater than 1x10-2 Pa and shall not deviate from adjacent poles by more than two orders of magnitude.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the vacuum bottle integrity test, the test specimen is considered to have passed the test.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand voltage test, the test specimen is considered to have passed the test.

  - Heaters shall be operational.

  - Protective device function test results shall be in accordance with Section 7.9.

  - Metering and instrumentation test results shall be in accordance with Section 7.11.

  - Instrument transformer test results shall be in accordance with Section 7.10.