# 7.       INSPECTION AND TEST PROCEDURES

# 7.25	Fiber-Optic Cables

# Visual and Mechanical Inspection

    - Compare cable, connector, and splice data with drawings and specifications.

    - Inspect cable and connections for physical and mechanical damage.

    - Verify that all connectors and splices are correctly installed.

# Optical Tests

    - Perform cable length measurement, fiber fracture inspection, and construction defect inspection using an optical time domain reflectometer.

    - Perform connector and splice integrity test using an optical time domain reflectometer.

    - Perform cable attenuation loss measurement with an optical power loss test set.

    - Perform connector and splice attenuation loss measurement from both ends of the optical cable with an optical power loss test set.

    - Perform transmit and receive power measurements from local device and remote device.

# Test Values – Visual and Mechanical

    - Cable and connections shall not have been subjected to physical or mechanical damage. (7.25.1.1)

    - Connectors and splices shall be installed in accordance with industry standards. (7.25.A.2)

# Test Values – Optical

    - The optical time domain reflectometer signal shall be analyzed for cable backscatter by viewing the reflected power/distance graph.

    - The optical time domain reflectometer signal shall be analyzed for excessive connection or splice attenuation by viewing the reflected power/distance graph.

    - Attenuation loss measurement shall be expressed in dB/km. Losses shall be within the manufacturer’s recommendations when no local site specifications are available.

    - Connector and splice attenuation loss measurement shall be expressed in dB/km. Losses shall be within the manufacturer’s recommendations when no local site specifications are available.

    - Transmit and receive power measurement results shall compare to manufacturer’s published data.

Page 204

ANSI/NETA ATS-2021