# 7.        INSPECTION AND TEST PROCEDURES

# 7.26	Electric Vehicle Charging Systems

## Visual and Mechanical Inspections

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition of cords and connectors.

  - Inspect anchorage, alignment, grounding, and required area clearances.

  - Verify the unit is clean and all shipping bracing, loose parts, and documentation shipped inside cubicles have been removed.

- Verify that wiring connections are tight and that wiring is secure to prevent damage during routine operation of moving parts.

- Inspect bolted electrical connections for high resistance using one or more of the following methods:

  - Use of a low-resistance ohmmeter in accordance with Section 7.26.B.1.

  - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

  - Perform thermographic survey in accordance with Section 9.

- Verify operation and sequencing of interlocking systems.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.26	Electric Vehicle Charging Systems (continued)

## Electrical Tests

  - Perform resistance measurements through bolted electrical connections with a low- resistance ohmmeter in accordance with Section 7.26.A.8.1.

  - Perform system function tests in accordance with manufacturer’s published data.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.26.A.8.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.12. (7.26.A.8.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.26.A.8.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Results of system function tests shall be in accordance with manufacturer’s published data.