# 7.        INSPECTIONS AND TEST PROCEDURES

# 7.3.3 Cables, Medium- and High-Voltage

## Visual and Mechanical Inspection

  - Compare cable data with drawings and specifications.

  - Inspect exposed sections of cables for physical damage.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.3.3.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform a thermographic survey in accordance with Section 9.

  - Inspect compression-applied connectors for correct cable match and indentation.

  - Inspect shield grounding, cable supports, and terminations.

  - Verify that visible cable bends meet or exceed ICEA and manufacturer’s minimum published bending radius.

*7.	Inspect fireproofing in common cable areas.

- If cables are terminated through window-type current transformers, inspect to verify that neutral and ground conductors are correctly placed and that shields are correctly terminated for operation of protective devices.

- Inspect for correct identification and arrangements.

- Inspect cable jacket and insulation condition.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.3.3.A.3.1.

  - Perform an insulation-resistance test individually on each conductor and each shield with all other conductors and shields grounded. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a shield-continuity test on each power cable by ohmmeter method.

7.       INSPECTIONS AND TEST PROCEDURES

7.3.3 Cables, Medium- and High-Voltage (continued)

*4.	Perform cable time domain reflectometer (TDR) measurements on each conductor.

- In accordance with ICEA, IEC, IEEE and other power cable consensus standards, testing can be performed by means of direct current, power frequency alternating current, very low frequency alternating current, or damped alternating current. These sources may be used to perform insulation-withstand tests, and baseline diagnostic tests such as partial discharge analysis, and power factor or dissipation factor. The selection shall be made after an evaluation of the available test methods and a review of the installed cable system. Some of the available test methods are listed below.

  - Dielectric Withstand

    - Direct current (dc) dielectric withstand voltage

    - Very low frequency (VLF) dielectric withstand voltage

    - Power frequency (50/60 Hz) dielectric withstand voltage

    - Damped alternating current (DAC) voltage

  - Baseline Diagnostic Tests

    - Power factor/dissipation factor (tan delta)

      - Power frequency (50/60 Hz)

      - Very low frequency (VLF)

      - Damped alternating current (DAC) voltage

    - DC insulation resistance

    - Partial discharge

      - Online (50/60 Hz)

      - Off line

        - Power Frequency (50/60 Hz)

        - Very low frequency (VLF)

        - Damped alternating current (DAC) voltage

7.        INSPECTIONS AND TEST PROCEDURES

7.3.3 Cables, Medium- and High-Voltage (continued)

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.3.3.A.3.1)

  - Bolt-torque levels should be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.3.3.A.3.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.3.3.A.3.3)

  - The minimum bend radius to which insulated cables may be bent for permanent training shall be in accordance with Table 100.22. (7.3.3.A.6)

## D	Test Values – Electrical

- Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

- Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

- Shielding shall exhibit continuity. Investigate resistance values in excess of ten ohms per 1000 feet of cable.

- TDR graphical measurements should clearly identify the cable length and characteristic should be consistent with other phases.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the test, the test specimen is considered to have passed the test.

  - Based on the test methodology chosen, refer to applicable standards or manufacturer’s literature for acceptable values.