7.      INSPECTION AND TEST PROCEDURES

7.4	Metal-Enclosed Busways (continued)

# Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify correct connection in accordance with single-line diagram.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.4.B.

    - Verify tightness of accessible bolted electrical connections and bus joints by calibrated torque-wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Confirm physical orientation in accordance with manufacturer’s labels to insure adequate cooling.

  - Verify “weep-hole” plugs are in accordance with manufacturer’s published data.

  - Verify correct installation of joint shield.

  - Verify ventilating openings are clean.

# Electrical Tests

  - Perform resistance measurements through bolted connections and bus joints with a low- resistance ohmmeter in accordance with Section 7.4.A.5.1.

  - Perform insulation resistance tests on each busway for one minute, phase-to-phase and phase-to-ground. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a dielectric withstand voltage test on each busway, phase-to-ground with phases not under test grounded, in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.17. Where no dc test value is shown in Table 100.17, an ac value shall be used. The test voltage shall be applied for one minute.

7.      INSPECTION AND TEST PROCEDURES

7.4	Metal-Enclosed Busways (continued)

  - Perform a contact-resistance test on each connection point of uninsulated busway. On insulated busway, measure resistance of assembled busway sections and compare values with the adjacent phases.

  - Perform phasing test on each busway tie section energized by separate sources. Tests must be performed from their permanent sources.

  - Verify operation of busway space heaters.

*7.	Perform online partial-discharge survey in accordance with Section 11.

# Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.4.A.5.1)

  - Bolt-torque levels should be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.4.A.5.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.4.A.5.3)

# Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance test voltages and resistance values shall be in accordance with manufacturer’s published data or Table 100.1. In the absence of manufacturer’s data, minimum resistance values are for a nominal 1000-foot busway run. Use the following formula to convert the measured resistance value to the 1000-foot nominal value:

R1000 ft = Measured Resistance x	Length of Run

1000

Converted values of insulation resistance less than those in Table 100.1 or manufacturer’s minimum should be investigated. Dielectric withstand voltage tests shall not proceed until insulation-resistance levels are raised above minimum values.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the test, the test specimen is considered to have passed the test.

7.      INSPECTION AND TEST PROCEDURES

7.4	Metal-Enclosed Busways (continued)

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. If manufacturer’s published data is not available, investigate values which deviate from those of similar bus connections and sections by more than 50 percent of the lowest value.

  - Phasing test results shall indicate the phase relationships are in accordance with system design.

  - Heaters shall be operational.

  - Results of online partial-discharge survey should be in accordance with manufacturer’s published data. In the absence of manufacturer’s published data, use Table 100.23.