# 7.       INSPECTION AND TEST PROCEDURES

# 7.5.1.2	Switches, Air, Medium-Voltage, Metal-Enclosed

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, grounding, and required clearances.

  - Verify the unit is clean.

  - Verify correct blade alignment, blade penetration, travel stops, arc interrupter operation, and mechanical operation.

  - Verify that fuse sizes and types are in accordance with drawings, short-circuit study, and coordination study.

  - Verify that expulsion-limiting devices are in place on all fuses having expulsion-type elements.

  - Verify that each fuseholder has adequate mechanical support and contact integrity.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.5.1.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify operation and sequencing of interlocking systems.

  - Verify correct phase barrier installation.

  - Verify correct operation of all indicating and control devices.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.5.1.2.A.9.1.

  - Measure contact resistance across each switchblade assembly and fuseholder.

# 7.      INSPECTION AND TEST PROCEDURES

# 7.5.1.2 Switches, Air, Medium-Voltage, Metal-Enclosed (continued)

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with switch closed, and across each open pole. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a dielectric withstand voltage test on each pole with switch closed. Test each pole- to-ground with all other poles grounded. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.2.

  - Measure fuse resistance.

  - Verify cubicle space heater operation.

*7.	Perform online partial-discharge survey in accordance with Section 11.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.5.1.2.A.9.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.5.1.2.A.9.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.5.1.2.A.9.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer's published data. If manufacturer's data is not available, investigate values that deviate from adjacent poles or similar switches by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. Dielectric withstand voltage tests shall not proceed until insulation-resistance levels are raised above minimum values.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand voltage test, the test specimen is considered to have passed the test.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.5.1.2	Switches, Air, Medium-Voltage, Metal-Enclosed (continued)

  - Investigate fuse resistance values that deviate from each other by more than 15 percent.

  - Heaters shall be operational.

  - Results of online partial-discharge survey shall be in accordance with manufacturer's published data. In the absence of manufacturer's data, refer to Table 100.23.