# 7.        INSPECTION AND TEST PROCEDURES

# 7.5.5	Switches, Cutouts

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, grounding, and required clearances.

  - Verify the unit is clean.

  - Verify correct blade alignment, blade penetration, travel stops, latching mechanism, and mechanical operation.

  - Verify that each fuseholder has adequate mechanical support and contact integrity.

  - Verify that fuse size and types are in accordance with drawings, short-circuit study, and coordination study.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.5.5.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter, in accordance with Section 7.5.5.A.8.1.

  - Measure contact resistance across each cutout.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with switch closed and across each open pole. Apply voltage in accordance with manufacturer's published data. In the absence of manufacturer's data, use Table 100.1.

  - Perform a dielectric withstand voltage test on each pole, phase-to-ground with cutout closed. Ground adjacent cutouts. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

7.        INSPECTION AND TEST PROCEDURES

7.5.5	Switches, Cutouts (continued)

  - Measure fuse resistance.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.5.5.A.8.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.5.5.A.8.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.5.5.A.8.3)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. If manufacturer’s published data is not available, investigate values which deviate from adjacent poles or similar switches by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated. Dielectric withstand voltage tests shall not proceed until insulation-resistance levels are raised above minimum values.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand voltage test, the test specimen is considered to have passed the test.

  - Investigate fuse resistance values that deviate from each other by more than 15 percent.