# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.1.1	Circuit Breakers, Air, Insulated-Case/Molded-Case

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage and alignment.

  - Verify the unit is clean.

  - Operate the circuit breaker to insure smooth operation.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.6.1.1.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Inspect operating mechanism, contacts, and arc chutes in unsealed units.

  - Perform adjustments for final protective device settings in accordance with the coordination study.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.6.1.1.A.6.1.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with the circuit breaker closed, and across each open pole. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a contact/pole-resistance test.

*4.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

- Determine long-time pickup and delay by primary current injection.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.1.1	Circuit Breakers, Air, Insulated-Case/Molded-Case (continued)

- Determine short-time pickup and delay by primary current injection.

- Determine ground-fault pickup and time delay by primary current injection.

- Determine instantaneous pickup by primary current injection.

*9.	Test functions of the trip unit by means of secondary injection.

- Perform minimum pickup voltage tests on shunt trip and close coils in accordance with manufacturer’s published data.

- Verify correct operation of auxiliary features such as trip and pickup indicators, zone interlocking, electrical close and trip operation, trip-free, anti-pump function, and trip unit battery condition. Reset all trip logs and indicators.

- Verify operation of charging mechanism.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.6.1.1.A.6.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.6.1.1.A.6.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.6.1.1.A.6.3)

  - Settings shall comply with coordination study recommendations. (7.6.1.1.A.8)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. If manufacturer’s published data is not available, investigate values that deviate from adjacent poles or similar breakers by more than 50 percent of the lowest value.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.6.1.1	Circuit Breakers, Air, Insulated-Case/Molded-Case (continued)

  - Long-time pickup values shall be as specified, and the trip characteristic shall not exceed manufacturer’s published time-current characteristic tolerance band, including adjustment factors. If manufacturer’s curves are not available, trip times shall not exceed the value shown in Table 100.7.

  - Short-time pickup values shall be as specified, and the trip characteristic shall not exceed manufacturer’s published time-current tolerance band.

  - Ground fault pickup values shall be as specified, and the trip characteristic shall not exceed manufacturer’s published time-current tolerance band.

  - Instantaneous pickup values shall be as specified and within manufacturer’s published tolerances. In the absence of manufacturer’s data, refer to Table 100.8.

  - Pickup values and trip characteristics shall be within manufacturer’s published tolerances.

  - Minimum pickup voltage of the shunt trip and close coils shall conform to the manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.20.

  - Breaker open, close, trip, trip-free, anti-pump, and auxiliary features shall function as designed.

  - The charging mechanism shall operate in accordance with manufacturer’s published data.