# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.1.2	Circuit Breakers, Low-Voltage Power

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify that all maintenance devices are available for servicing and operating the breaker.

  - Verify the unit is clean.

  - Verify the arc chutes are intact.

  - Inspect moving and stationary contacts for condition and alignment.

  - Verify that primary and secondary contact wipe and other dimensions vital to satisfactory operation of the breaker are correct.

  - Perform all mechanical operator and contact alignment tests on both the breaker and its operating mechanism in accordance with manufacturer’s published data.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.6.1.2.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform a thermographic survey in accordance with Section 9.

  - Verify cell fit and element alignment.

  - Verify racking mechanism operation.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

  - Perform adjustments for final protective device settings in accordance with coordination study provided by end user.

  - Record as-found and as-left operation counter readings.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.6.1.2	Circuit Breakers, Low-Voltage Power (continued)

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.6.1.2.A.10.1.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with the circuit breaker closed, and across each open pole. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a contact/pole-resistance test.

*4.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

- Determine long-time pickup and delay by primary current injection.

- Determine short-time pickup and delay by primary current injection.

- Determine ground-fault pickup and delay by primary current injection.

- Determine instantaneous pickup value by primary current injection.

*9.	Test functions of the trip unit by means of secondary injection.

- Perform minimum pickup voltage tests on shunt trip and close coils in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.20.

- Verify correct operation of any auxiliary features such as trip and pickup indicators, zone interlocking, electrical close and trip operation, trip-free, antipump function, and trip unit battery condition. Reset all trip logs and indicators.

- Verify operation of charging mechanism.

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.6.1.2.A.10.1).

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.6.1.2.A.10.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.6.1.2.A.10.3)

# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.1.2	Circuit Breakers, Low-Voltage Power (continued)

  - Settings shall comply with coordination study recommendations. (7.6.1.2.A.14)

  - Operations counter shall advance one digit per close-open cycle. (7.6.1.2.A.15)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values of circuit breakers shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. In the absence of manufacturer’s data, investigate values that deviate from adjacent poles or similar breakers by more than 50 percent of the lowest value.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - Long-time pickup values shall be as specified, and the trip characteristic shall not exceed manufacturer’s published time-current characteristic tolerance band, including adjustment factors. If manufacturer’s curves are not available, trip times shall not exceed the value shown in Table 100.7.

  - Short-time pickup values shall be as specified, and the trip characteristic shall not exceed manufacturer’s published time-current tolerance band.

  - Ground fault pickup values shall be as specified, and the trip characteristic shall not exceed manufacturer’s published time-current tolerance band.

  - Instantaneous pickup values shall be as specified and within manufacturer’s published tolerances. In the absence of manufacturer’s data, use Table 100.8.

  - Pickup values and trip characteristic shall be as specified and within manufacturer’s published tolerances.

  - Minimum pickup voltage of the shunt trip and close coils shall conform to the manufacturer’s published data. In the absence of the manufacturer’s published data, refer to Table 100.20.

  - Auxiliary features shall operate in accordance with manufacturer’s published data.

  - The charging mechanism shall operate in accordance with manufacturer’s published data.