# 7.       INSPECTION AND TEST PROCEDURES

# 7.6.1.3	Circuit Breakers, Air, Medium-Voltage

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify that all maintenance devices are available for servicing and operating the breaker.

  - Verify the unit is clean.

  - Verify the arc chutes are intact.

  - Inspect moving and stationary contacts for condition and alignment.

  - If recommended by manufacturer, slow close/open breaker and check for binding, friction, contact alignment, and penetration. Verify that contact sequence is in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use IEEE C37.04.

  - Perform all mechanical operation tests on the operating mechanism in accordance with manufacturer’s published data.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of a low-resistance ohmmeter in accordance with Section 7.6.1.3.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data or Table 100.12.

    - Perform a thermographic survey in accordance with Section 9.

  - Verify cell fit and element alignment.

  - Verify racking mechanism operation.

  - Inspect puffer operation.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

  - Perform contact-timing test.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.1.3	Circuit Breakers, Air, Medium-Voltage (continued)

*16.	Perform mechanism-motion analysis.

*17.	Perform trip/close coil current signature analysis.

18.	Record as-found and as-left operation-counter readings.

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter. See Section 7.6.1.3.A.10.1.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with circuit breaker closed, and across each open pole. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a contact/pole-resistance test.

*4.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be on minute. For units with solid-state components or control devices that cannot tolerate the applied voltage, follow manufacturer’s recommendation.

- With breaker in the test position, make the following tests:

  - Trip and close breaker with the control switch.

  - Trip breaker by operating each of its protective relays.

  - Verify mechanism charge, trip-free, and antipump functions.

- Perform minimum pickup voltage tests on trip and close coils in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.20.

*7.	Perform power-factor or dissipation-factor tests with breaker in both the open and closed positions.

*8.	Perform power-factor or dissipation-factor tests on each bushing equipped with a power- factor/capacitance tap. In the absence of a power-factor/ capacitance tap, perform hot-collar tests. These tests shall be in accordance with the test equipment manufacturer’s published data.

- Perform a dielectric withstand voltage test on each phase with the circuit breaker closed and the poles not under test grounded. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.19.

- Measure blowout coil circuit resistance.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.1.3	Circuit Breakers, Air, Medium-Voltage (continued)

- Verify operation of heaters.

- Test instrument transformers in accordance with Section 7.10.

## Test Values – Visual and Mechanical

  - Mechanical operation and contact alignment shall be in accordance with manufacturer’s published data. (7.6.1.3.A.9)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.6.1.3.A.10.1)

3,	Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.6.1.3.A.10.2)

- Results of the thermographic survey shall be in accordance with Section 9. (7.6.1.3.A.10.3)

- Contact timing values shall be in accordance with manufacturer’s published data. (7.6.1.3.A.15)

- Travel and velocity values shall be in accordance with manufacturer’s published data. (7.6.1.3.A.16)

- Trip/close coil current values shall be in accordance with manufacturer’s published data. (7.6.1.3.A.17)

6.	Operations counter shall advance one digit per close-open cycle. (7.6.1.3.A.18)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values of circuit breakers shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. In the absence of manufacturer’s data, investigate values that deviate from adjacent poles or similar breakers by more than 50 percent of the lowest value.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.6.1.3	Circuit Breakers, Air, Medium-Voltage (continued)

  - Breaker mechanism charge, close, open, trip, trip-free, and antipump features shall function as designed.

  - Minimum pickup voltage of the trip and close coils shall conform to the manufacturer’s published data. In the absence of the manufacturer’s published data, refer to Table 100.20.

  - Power-factor or dissipation-factor values shall be compared with previous test results of similar breakers or manufacturer’s published data.

  - Power-factor or dissipation-factor and capacitance values shall be within ten percent of nameplate rating for bushings. Hot collar tests are evaluated on a milliampere/milliwatt loss basis, and the results shall be compared to values of similar bushings.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the circuit breaker is considered to have passed the test.

  - The blowout coil circuit shall exhibit continuity.

  - Heaters shall be operational.

  - The results of instrument transformer tests shall be in accordance with Section 7.10.