# 7.       INSPECTIONS AND TEST PROCEDURES

# 7.6.3	Circuit Breakers, Vacuum, Medium-Voltage

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify that all maintenance devices such as special tools and gauges specified by the manufacturer are available for servicing and operating the breaker.

  - Verify the unit is clean.

  - Perform all mechanical operation tests on the operating mechanism in accordance with manufacturer’s published data.

  - Measure critical distances such as contact gap as recommended by manufacturer.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.6.3.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify cell fit and element alignment.

  - Verify racking mechanism operation.

  - Verify appropriate lubrication on moving, current-carrying parts and on moving and sliding surfaces.

  - Perform contact-timing test.

*13.	Perform trip/close coil current signature analysis.

*14.	Perform mechanism motion analysis.

15.	Record as-found and as-left operation counter readings.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.6.3	Circuit Breakers, Vacuum, Medium-Voltage (continued)

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.6.3.A.8.1.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with the circuit breaker closed, and across each open pole. Test voltage shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

*3.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components, follow manufacturer’s recommendation.

- Perform a contact/pole-resistance test.

- Perform minimum pickup voltage tests on trip and close coils in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.20.

- Verify correct operation of any auxiliary features such as electrical close and trip operation, trip-free, and antipump function.

- Trip circuit breaker by operation of each protective device. Reset all trip logs and indicators.

*8.	Perform power-factor or dissipation-factor tests on each pole with the breaker open and each phase with the breaker closed.

*9.	Perform power-factor or dissipation-factor tests on each bushing equipped with a power- factor/capacitance tap. In the absence of a power-factor/capacitance tap, perform hot-collar tests. These tests shall be in accordance with the test equipment manufacturer’s published data.

*10	Perform magnetron atmospheric condition (MAC) test on each vacuum interrupter.

- Perform vacuum bottle integrity (dielectric withstand voltage) test across each vacuum bottle with the breaker in the open position in strict accordance with manufacturer’s published data.

- Perform a dielectric withstand voltage test in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.19.

- Verify operation of heaters.

- Test instrument transformers in accordance with Section 7.10.

# INSPECTION AND TEST PROCEDURES

# 7.6.3	Circuit Breakers, Vacuum, Medium-Voltage (continued)

## Test Values – Visual and Mechanical

  - Critical distance measurements such as contact gap shall be in accordance with the manufacturer’s published data. (7.6.3.A.7)

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.6.3.A.8.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.6.3.A.8.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.6.3.A.8.3)

  - Contact timing values shall be in accordance with manufacturer’s published data. (7.6.3.A.12)

  - Trip/close coil current values shall be in accordance with manufacturer’s published data. (7.6.3.A.13)

  - Travel and velocity values shall be in accordance with manufacturer’s published data. (7.6.3.A.14)

  - Operation counter shall advance one digit per close-open cycle. (7.6.3.A.15)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation-resistance values of circuit breakers shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations should be investigated.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. In the absence of manufacturer’s data, investigate values that deviate from adjacent poles or similar breakers by more than 50 percent of the lowest value.

  - Minimum pickup voltage of the trip and close coils shall conform to the manufacturer’s published data. In the absence of the manufacturer’s published data, refer to Table 100.20.

  - Auxiliary features shall operate in accordance with manufacturer’s published data.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.6.3	Circuit Breakers, Vacuum, Medium-Voltage (continued)

  - Protective devices shall operate the breaker per system design.

  - Power-factor or dissipation-factor values shall be compared to manufacturer’s published data. In the absence of manufacturer’s data the comparison shall be made to similar breakers.

  - Power-factor or dissipation-factor and capacitance values shall be within ten percent of nameplate rating for bushings. Hot collar tests are evaluated on a milliampere/milliwatt loss basis, and the results should be compared to values of similar bushings.

  - In the absence of manufacturer’s published data, each vacuum interrupter pressure shall not be greater than 1x10-2 Pa and shall not deviate from adjacent poles by more than two orders of magnitude.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the vacuum bottle integrity test, the test specimen is considered to have passed the test.

  - If no evidence of distress or insulation failure is observed by the end of the total time of voltage application during the dielectric withstand test, the test specimen is considered to have passed the test.

  - Heaters shall be operational.

  - Results of instrument transformer tests shall be in accordance with Section 7.10.