# 7.        INSPECTION AND TEST PROCEDURES

# 7.8	Network Protectors, 600-Volt Class

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect physical and mechanical condition.

  - Inspect anchorage, alignment, and grounding.

  - Verify the unit is clean.

  - Verify arc chutes are intact.

  - Inspect moving and stationary contacts for condition and alignment.

  - Verify that maintenance devices are available for servicing and operating the network protector.

  - Verify that primary and secondary contact wipe and other dimensions vital to satisfactory operation of the network protector are correct.

  - Perform mechanical operator and contact alignment tests on both the protector and its operating mechanism.

  - Inspect bolted electrical connections for high resistance using one or more of the following methods:

    - Use of low-resistance ohmmeter in accordance with Section 7.8.B.1.

    - Verify tightness of accessible bolted electrical connections by calibrated torque- wrench method in accordance with manufacturer's published data. In the absence of manufacturer's data, use Table 100.12.

    - Perform thermographic survey in accordance with Section 9.

  - Verify cell fit and element alignment.

  - Verify racking mechanism operation.

  - Verify appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces.

  - Record as-found and as-left operation counter readings.

  - Perform a leak test on submersible enclosure in accordance with manufacturer’s published data.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.8	Network Protectors, 600-Volt Class (continued)

## Electrical Tests

  - Perform resistance measurements through bolted connections with a low-resistance ohmmeter in accordance with Section 7.8.A.10.1.

  - Perform insulation-resistance tests for one minute on each pole, phase-to-phase and phase- to-ground with network protector closed, and across each open pole. Apply voltage in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1.

  - Perform a contact/pole-resistance test.

*4.	Perform insulation-resistance tests on all control wiring with respect to ground. Applied potential shall be 500 volts dc for 300-volt rated cable and 1000 volts dc for 600-volt rated cable. Test duration shall be one minute. For units with solid-state components or for control devices that cannot tolerate the voltage, follow manufacturer’s recommendation.

- Verify current transformer ratios in accordance with Section 7.10.

- Measure the resistance of each network protector power fuse.

- Measure minimum pickup voltage of the motor control relay.

- Verify that the motor can charge the closing mechanism at the minimum voltage specified by the manufacturer.

- Measure minimum pickup voltage of the trip actuator. Verify that the actuator resets correctly.

- Calibrate the network protector relays in accordance with Section 7.9.

- Perform operational tests.

  - Verify correct operation of all mechanical and electrical interlocks.

  - Verify trip-free operation.

  - Verify correct operation of the auto-open-close control handle.

  - Verify the protector will close with voltage on the transformer side only.

  - Verify the protector will open when the source feeder breaker is opened.

- Verify phase rotation, phasing, and synchronized operation as required by the application.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.8	Network Protectors, 600-Volt Class (continued)

## Test Values – Visual and Mechanical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value. (7.8.A.10.1)

  - Bolt-torque levels shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.12. (7.8.A.10.2)

  - Results of the thermographic survey shall be in accordance with Section 9. (7.8.A.10.3)

  - Operations counter shall advance one digit per close-open cycle. (7.8.A.14)

## Test Values – Electrical

  - Compare bolted connection resistance values to values of similar connections. Investigate values which deviate from those of similar bolted connections by more than 50 percent of the lowest value.

  - Insulation resistance of the network protector shall be in accordance with manufacturer’s published data. In the absence of manufacturer’s data, use Table 100.1. Values of insulation resistance less than this table or manufacturer’s recommendations shall be investigated.

  - Microhm or dc millivolt drop values shall not exceed the high levels of the normal range as indicated in the manufacturer’s published data. In the absence of manufacturer’s data, investigate values that deviate from adjacent poles or similar protectors by more than 50 percent of the lowest value.

  - Insulation-resistance values of control wiring shall not be less than two megohms.

  - Results of current transformer ratios shall be in accordance with Section 7.10.

  - Investigate fuse resistance values that deviate from each other by more than 15 percent.

  - Minimum pickup voltage of the motor control relay shall be in accordance with manufacturer’s published data, but not more than 75 percent of rated control circuit voltage.

  - Minimum acceptable motor closing voltage should not exceed 75 percent of rated control circuit voltage.

  - Trip actuator minimum pickup voltage shall not exceed 75 percent of rated control circuit voltage.

  - Results of network protector relay calibrations shall be in accordance with Section 7.9.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.8	Network Protectors, 600-Volt Class (continued)

  - Network protector operation shall be in accordance with design requirements.

  - Phase rotation, phasing, and synchronizing shall be in accordance with system design requirements.