# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.1 Protective Relays, Electromechanical and Solid-State

## Visual and Mechanical Inspection

  - Compare equipment nameplate data with drawings and specifications.

  - Inspect relays and cases for physical damage. Remove shipping restraint material.

  - Verify the unit is clean.

  - Inspect the unit.

    - Relay Case

      - Tighten case connections.

      - Inspect cover for correct gasket seal.

      - Inspect shorting hardware, connection paddles, and knife switches.

      - Remove any foreign material from the case.

      - Verify target reset.

      - Clean cover glass.

    - Relay

      - Inspect relay for foreign material, particularly in disk slots of the damping and electromagnets.

      - Verify disk clearance throughout its travel. Verify contact follow and spring tension.

      - Inspect spiral spring convolutions.

      - Inspect disk and contacts for freedom of movement and correct travel.

      - Verify tightness of mounting hardware and connections.

      - Burnish contacts.

      - Inspect bearings and pivots.

  - Verify that all settings are in accordance with coordination study or setting sheet supplied by owner.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.1 Protective Relays, Electromechanical and Solid-State (continued)

## Electrical Tests

  - Perform an insulation-resistance test on each circuit-to-frame. Procedures for performing insulation-resistance tests on solid-state relays shall be determined from the relay manufacturer’s published data.

  - Test targets and indicators.

    - Determine pickup and dropout of electromechanical targets.

    - Verify operation of all light-emitting diode indicators.

    - Set contrast for liquid-crystal display readouts.

  - Protection Elements

    - 2/62 Timing Relay

      - Determine time delay.

      - Verify operation of all contacts used in the control scheme.

    - 21 Distance Relay

      - Determine maximum reach.

      - Determine maximum torque angle and directional characteristic.

      - Determine offset.

      - Plot impedance circle.

    - 24 Volts/Hertz Relay

      - Determine pickup frequency at rated voltage.

      - Determine pickup frequency at a second voltage level.

      - Determine time delay.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.1 Protective Relays, Electromechanical and Solid-State (continued)

    - 25 Sync Check Relay

      - Determine closing zone at rated voltage.

      - Determine maximum voltage differential that permits closing at zero degrees.

      - Determine live line, live bus, dead line, and dead bus set points.

      - Determine time delay.

      - Determine advanced closing angle.

      - Verify dead bus/live line, dead line/live bus and dead bus/dead line control functions.

    - 27 Undervoltage Relay

      - Determine dropout voltage.

      - Determine time delay.

      - Determine time delay at a second point on the timing curve for inverse time relays.

    - 32 Directional Power Relay

      - Determine directional unit maximum torque angle.

      - Determine directional unit contact closing zone.

      - Determine directional unit minimum pickup at maximum torque angle.

      - Determine time delay.

      - Verify time delay at a second point on the timing curve for inverse time relays.

      - Plot the operating characteristic.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.1 Protective Relays, Electromechanical and Solid-State (continued)

      - 40 Loss of Field (Impedance) Relay

        - Determine maximum torque angle.

        - Determine maximum reach.

        - Determine offset.

        - Test for spurious torque.

        - Plot impedance circle.

      - 46 Current Balance Relay

        - Determine pickup of each unit.

        - Determine percent slope.

        - Determine time delay with zero restraint.

      - 46N Negative Sequence Current Relay

        - Determine negative sequence alarm level.

        - Determine negative sequence minimum trip level.

        - Determine maximum time delay.

        - Verify two points on the (I2)2t curve.

      - 47 Phase Sequence or Phase Balance Voltage Relay

        - Determine positive sequence voltage to close the normally open contact.

        - Determine positive sequence voltage to open the normally closed contact (undervoltage trip).

        - Verify negative sequence trip.

        - Determine time delay to close the normally open contact with sudden application of 120 percent of pickup.

        - Determine time delay to close the normally closed contact upon removal of voltage when previously set to rated system voltage.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.1 Protective Relays, Electromechanical and Solid-State (continued)

      - 49R Thermal Replica Relay

        - Determine time delay at 300 percent of setting.

        - Determine a second point on the operating curve.

        - Determine minimum pickup.

      - 49T Temperature (RTD) Relay

        - Determine trip resistance.

        - Determine reset resistance.

      - 50 Instantaneous Overcurrent Relay

        - Determine pickup.

        - Determine dropout.

        - Determine element time delay.

      - 50BF Breaker Failure

        - Determine current supervision pickup.

        - Determine time delays.

        - Test all initiate inputs and used outputs.

      - 51 Time Overcurrent

        - Determine minimum pickup.

        - Determine time delay at two points on the time current curve.

      - 55 Power Factor Relay

        - Determine tripping lead and lag angle.

        - Determine enable time delay.

        - Determine operate time delay.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.1 Protective Relays, Electromechanical and Solid-State (continued)

      - 59 Overvoltage Relay

        - Determine overvoltage pickup.

        - Determine time delay to close the contact with sudden application of 120 percent of pickup.

      - 60 Voltage Balance Relay

        - Determine voltage difference to close the contacts with one source at rated voltage.

        - Plot the operating curve for the relay.

      - 63 Transformer Sudden Pressure Relay

        - Determine rate-of-rise or the pickup level of suddenly applied pressure in accordance with manufacturer’s published data.

        - Verify operation of the 63 FPX seal-in circuit.

        - Verify trip circuit to remote operating device.

      - 64 Ground Detector Relay

        - Determine maximum impedance to ground causing relay pickup.

      - 67 Directional Overcurrent Relay

        - Determine directional unit minimum pickup at maximum torque angle.

        - Determine contact closing zone.

        - Determine maximum torque angle.

        - Plot operating characteristics.

        - Determine overcurrent unit pickup.

        - Determine overcurrent unit time delay at two points on the time current curve.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.1 Protective Relays, Electromechanical and Solid-State (continued)

      - 79 Reclosing Relay

        - Determine time delay for each programmed reclosing interval.

        - Verify lockout for unsuccessful reclosing.

        - Determine reset time.

        - Determine close pulse duration.

        - Verify instantaneous overcurrent lockout.

      - 81 Frequency Relay

        - Verify frequency set points.

        - Determine time delay.

        - Determine undervoltage cutoff.

      - 85 Pilot Wire Monitor

        - Determine overcurrent pickup.

        - Determine undercurrent pickup.

        - Determine pilot wire ground pickup level.

      - 87 Differential

        - Determine operating unit pickup.

        - Determine the operation of each restraint unit.

        - Determine slope.

        - Determine harmonic restraint.

        - Determine instantaneous pickup.

        - Plot operating characteristics for each restraint.

  - Control Verification/Functional Tests

Verify that each of the relay contacts performs its intended function in the control scheme including breaker trip tests, close inhibit tests, 86 lockout tests, and alarm functions. Refer to Section 8.

# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.1 Protective Relays, Electromechanical and Solid-State (continued)

## Test Values – Visual and Mechanical

  - Relay Case

    - Case connections shall be torqued in accordance with manufacturer’s published data. (7.9.1.A.4.1.1)

    - Cover gasket shall be intact and able to prevent foreign matter from entering the case. (7.9.1.A.4.1.2)

    - Cover glass, connection paddles, and/or knife switches shall be clean. (7.9.1.A.4.1.3)

    - Case shall be free of foreign material. (7.9.1.A.4.1.4)

    - The target reset shall be operational. (7.9.1.A.4.1.5)

  - Relay

    - Relay shall be free of foreign material. (7.9.1.A.4.2.1)

    - Relay disc clearance, contact clearance, and spring bias shall operate in accordance with manufacturer’s published data. (7.9.1.A.4.2.2)

    - Relay spiral spring shall be concentric. (7.9.1.A.4.2.3)

    - Relay discs and contacts shall have freedom of movement and correct travel distance in accordance with manufacturer’s published data. (7.9.1.A.4.2.4)

    - Mounting hardware and connections shall be tightened to the manufacturer’s recommended torque values. (7.9.1.A.4.2.5)

    - Contacts shall be clean and make good contact with each other. (7.9.1.A.4.2.6)

    - Bearings and pivots shall be clean and allow freedom of movement. (7.9.1.A.4.2.7)

  - Relay settings shall match the coordination study or setting sheet supplied by owner. (7.9.1.A.5)

# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.1 Protective Relays, Electromechanical and Solid-State (continued)

## Test Values – Electrical

  - Insulation-resistance values shall be in accordance with manufacturer’s published data. Values of insulation resistance less than the manufacturer’s recommendations shall be investigated.

  - Targets and Indicators

    - Pickup and dropout of electromechanical targets shall be in accordance with manufacturer’s published data.

    - Light-emitting diodes shall illuminate.

  - Operation of protection elements for devices listed in Section 7.9.1.B, 1 through 25, shall be calibrated using manufacturer’s recommended tolerances and at critical test points specified by the setting engineer.

  - Control Verification

    - Control verification outputs and protection schemes, as listed in Section 7.9.1.B.4, shall operate as per the design. Results shall be within the manufacturer’s published tolerances.

    - When critical test points are specified, the relay shall be calibrated to those points even though other test points may be out of tolerance.