# 7.       INSPECTION AND TEST PROCEDURES

# 7.9.2	Protective Relays, Microprocessor-Based

## Visual and Mechanical Inspection

  - Record model number, style number, serial number, firmware revision, software revision, and rated control voltage.

  - Verify operation of light-emitting diodes, display, and targets.

  - Record passwords for all access levels.

  - Clean the front panel and remove foreign material from the case.

  - Check tightness of connections.

  - Verify that the frame is grounded in accordance with manufacturer’s instructions.

  - Set the relay in accordance with the engineered setting file and coordination study.

  - Download settings and logic from the relay and compare the settings to those specified in the coordination study or setting sheet supplied by owner.

  - Set clock if not controlled externally and verify relay displays the correct date and time.

  - Check with setting engineer for applicable firmware updates and product recalls.

  - Inspect, clean, and verify operation of shorting devices.

## Electrical Tests

  - Perform insulation-resistance tests from each circuit to the grounded frame in accordance with manufacturer’s published data.

  - Apply voltage or current to all analog inputs and verify correct registration of the relay meter functions.

  - Verify SCADA metering values at remote terminals.

  - Protection Elements

Check functional operation of each element used in the protection scheme as described for electromechanical and solid-state relays in 7.9.1.B.3. When not otherwise specified, use manufacturer’s recommended tolerances.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.9.2	Protective Relays, Microprocessor-Based (continued)

  - Control Verification

    - Check operation of all active digital inputs.

    - Check all output contacts or SCRs, preferably by operating the controlled device such as circuit breaker, auxiliary relay, or alarm.

    - Check all internal logic functions used in the protection scheme.

    - For pilot schemes, perform protection system communication tests.

    - Upon completion of testing, reset all min/max records and fault counters. Delete sequence-of-events records and all event records.

  - Arc Energy Reduction Systems

    - Determine pickup for all overcurrent elements used.

    - Determine timing for all overcurrent elements used.

    - Verify zone interlocking logic and timing.

    - Verify logic for normal and maintenance modes of operation.

    - Verify communication failure and circuit monitoring alarms.

    - Verify ambient light for each light sensor and verify relay light sensor pickup values are above maximum ambient values.

    - Verify each light sensor logic and timing.

    - Verify current supervision logic and timing.

    - Verify differential scheme logic and timing. Verify that all current transformers used in the differential zone have been tested in accordance with Section 7.10.1.B of this standard.

  - Verify trip and close coil monitoring functions.

  - Verify setting change alarm to SCADA.

  - Verify relay SCADA communication and indications such as protection operate, protection fail, communication fail, fault recorder trigger.

  - Verify all communication links are operational.

# 7.        INSPECTION AND TEST PROCEDURES

# 7.9.2	Protective Relays, Microprocessor-Based (continued)

## Test Values – Visual and Mechanical

  - Light-emitting diodes, displays, and targets should illuminate. (7.9.2.A.2)

  - Relay should be clean and operational. (7.9.2.A.4)

  - Settings and logic should agree with the most recent engineered setting files. (7.9.2.A.8)

  - Verify relay displays the correct date and time. (7.9.2.A.10)

## Test Values – Electrical

  - Insulation-resistance values should be in accordance with manufacturer’s published data. Values of insulation resistance less than manufacturer’s recommendations should be investigated.

  - Voltage and current analog readings should be in accordance with manufacturer’s published tolerances.

  - SCADA metering values should function in accordance with the manufacturer’s published data.

  - Operation of protection elements for devices as listed in 7.9.1.B, items 1 through 25, should be operational and within manufacturer’s recommended tolerances.

  - Control verification inputs, outputs, and protection schemes, as listed in 7.9.2.B.5, items 1 through 9, should operate as per the design. Results should be within the manufacturer’s published tolerances.

  - Operation of protection elements for arc energy reduction systems listed in 7.9.2.B.6, items 1 through 9, shall be operational and in accordance with manufacturer’s published data.