## RESA XFMR Test Results (hidden)
www.resapower.com
MV XFMR TEST RESULT SUMMARY | [16 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  | 559082 |  |  | DATE: |  |  | 2025-01-11 |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  | STURGEON ELECTRIC |  |  | TESTED BY: |  |  | AP/TD | [7 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  | TPG CAT MODERNIZATION |  |  | APPROVED BY: |  |  | J. SWENSON | [7 empty] | PROOF TEST
| DEVICE ID | RATING IN KVA | SERIAL NUMBER |  | POWER FACTOR | EXCITATION |  | INSULATION RESISTANCE | TURNS RATIO |  | WINDING RESISTANCE | BUSHINGS & ARRESTERS |  | CURRENT TRANSFORMER | OIL ANALYSIS |  |  |  | NOTES
www.resapower.com
MV XFMR TEST RESULT SUMMARY | [16 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  | 559082 |  |  | DATE: |  |  | 2025-01-11 |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  | STURGEON ELECTRIC |  |  | TESTED BY: |  |  | AP/TD | [7 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  | TPG CAT MODERNIZATION |  |  | APPROVED BY: |  |  | J. SWENSON | [7 empty] | PROOF TEST
| DEVICE ID | RATING IN KVA | SERIAL NUMBER |  | POWER FACTOR | EXCITATION |  | INSULATION RESISTANCE | TURNS RATIO |  | WINDING RESISTANCE | BUSHINGS & ARRESTERS |  | CURRENT TRANSFORMER | OIL ANALYSIS |  |  |  | NOTES
Note on CN9: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on CN64: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P

## RESA MV Cable Test Results (hidden)
www.resapower.com
MV CABLE TEST RESULT SUMMARY | [16 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  | 559082 |  |  | DATE: |  |  | 2025-01-21 |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  | STURGEON ELECTRIC |  |  | TESTED BY: |  |  | AP/TD | [7 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  | TPG CAT MODERNIZATION |  |  | APPROVED BY: |  |  | J. SWENSON | [7 empty] | PROOF TEST
| CABLE ID | LENGTH | TYPE/INSULATION |  | RATED VOLTAGE | SIZE |  | FORMATION | SOURCE LOCATION |  | TERMINATION LOCATION | INSULATION RESISTANCE |  | VLF | NOTES
www.resapower.com
MV CABLE TEST RESULT SUMMARY | [16 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  | 559082 |  |  | DATE: |  |  | 2025-01-21 |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  | STURGEON ELECTRIC |  |  | TESTED BY: |  |  | AP/TD | [7 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  | TPG CAT MODERNIZATION |  |  | APPROVED BY: |  |  | J. SWENSON | [7 empty] | PROOF TEST
| CABLE ID | LENGTH | TYPE/INSULATION |  | RATED VOLTAGE | SIZE |  | FORMATION | SOURCE LOCATION |  | TERMINATION LOCATION | INSULATION RESISTANCE |  | VLF | NOTES
ACCEPTABLE
NOT ACCEPTABLE
SEE NOTES
Note on CN9: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on CN64: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P

## Project Alpha LV Tracker
Create a Project Schedule in this worksheet. Enter title of this project in cell B1. Information about how to use this worksheet, including instructions for screen readers and the author of this workbook is in the About worksheet. Continue navigating down column A to hear further instructions. | Project Alpha:
RESA Power Project Manager: Jason Swenson
Enter the name of the Project Lead in cell B3. Enter the Project Start date in cell E3. Project Start: label is in cell C3. | RESA Power Lead Technician: Austin Painter |  | Project Start: | [6 empty] | 2025-07-01
The Display Week in cell E4 represents the starting week to display in the project schedule in cell I4. The project start date is considered Week 1. To change the display week, simply enter a new week number in cell E4. The starting date for each week, starting with the display week from cell E4, starts in cell I4 and is auto calculated. There are 8 weeks represented in this view from cell I4 through cell BF4. You should not modify these cells. Display Week: label is in cell C4. | 2025-08-25 |  | Display Week: | [6 empty] | 3 |  |  | 2025-07-14 | [6 empty] | 2025-07-21 | [6 empty] | 2025-07-28 | [6 empty] | 2025-08-04 | [6 empty] | 2025-08-11 | [6 empty] | 2025-08-18 | [6 empty] | 2025-08-25 | [6 empty] | 2025-09-01
Cells I5 through BL5 contain the day number for the week represented in the cell block above each date cell and are auto calculated. You should not modify these cells. Today's date is outlined in Red (hex #AD3815) from today's date in row 5 through the entire date column to the end of the project schedule. | time axis 2025-07-14 to 2025-09-07
This row contains headers for the project schedule that follows below them. Navigate from B6 through BL 6 to hear the content. The first letter of each day of the week for the date above that heading, starts in cell I6 and continues through cell BL6. All project timeline charting is auto generated based on the start and end dates entered, using conditional formats. Do not modify content in cells within columns after column I starting with cell I7. | Task | Task Info | Qty on Site | Qty Completed | Hours / Unit | Total Hours | Hours Remaining | Progress | Comments | START | END | DAYS | time axis 2025-07-14 to 2025-09-07
Do not delete this row. This row is hidden to preserve a formula that is used to highlight the current day within the project schedule.
The cell at right contains the Phase 2 sample title. You can create a new phase at any time within column B. This project schedule does not require phases. To remove the phase, simply delete the row. To create a new phase block in this row, enter a new Title in cell at right. To continue adding tasks to the phase above, enter a new row above this one and fill in the task data as in cell A9's instruction. Update the Phase details in cell at right based on cell A8's instruction. Continue navigating down column A cells to learn more. If you haven't added any new rows in this worksheet, you will find 2 additional sample phase blocks have been created for you in cells B20 and B26. Otherwise, navigate through column A cells to find the additional blocks. Repeat the instructions from cells A8 and A9 whenever you need to. | SCOPE 1 | Emergency Generator Distribution |  |  |  | 101 | 89 | 11.88% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.1 | LV Switchboards | 2 | 0 | 4 | 8 | 8 | 0% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.2 | LV Circuit Breakers Primary Injection | 6 | 0 | 3 | 18 | 18 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.3 | LV ATS' (Hi-Potential & DLRO) | 7 | 3 | 4 | 28 | 16 | 42.86% |  | 2025-07-01 | 2025-09-01
| Task 1.4 | LV Distribution Panels | 3 | 0 | 4 | 12 | 12 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.5 | LV Panelboards | 26 | 0 | 1 | 26 | 26 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.6 | LV MCB Secondary Injection | 8 | 0 | 0.5 | 4 | 4 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.7 | LV Dry-Type Transformer | 4 | 0 | 1.25 | 5 | 5 | 0% |  | 2025-07-01 | 2025-09-01
The cell at right contains the Phase 2 sample title. You can create a new phase at any time within column B. This project schedule does not require phases. To remove the phase, simply delete the row. To create a new phase block in this row, enter a new Title in cell at right. To continue adding tasks to the phase above, enter a new row above this one and fill in the task data as in cell A9's instruction. Update the Phase details in cell at right based on cell A8's instruction. Continue navigating down column A cells to learn more. If you haven't added any new rows in this worksheet, you will find 2 additional sample phase blocks have been created for you in cells B20 and B26. Otherwise, navigate through column A cells to find the additional blocks. Repeat the instructions from cells A8 and A9 whenever you need to. | SCOPE 2 | Datacenter Main Distribution |  |  |  | 85 | 85 | 0% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.1 | LV Isolation-Bypass ATS' (Hi-Potential & DLRO) | 2 | 0 | 4 | 8 | 8 | 0% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.2 | LV Distribution Boards | 4 | 0 | 4 | 16 | 16 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.3 | LV Circuit Breakers Primary Injection | 10 | 0 | 3 | 30 | 30 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.4 | LV Distribution Panels | 2 | 0 | 4 | 8 | 8 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.5 | LV Panelboards | 1 | 0 | 1 | 1 | 1 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.6 | LV Large Dry-Type Transformer | 2 | 0 | 4 | 8 | 8 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.7 | LV MCB Secondary Injection | 28 | 0 | 0.5 | 14 | 14 | 0% |  | 2025-07-01 | 2025-09-01
The cell at right contains the Phase 2 sample title. You can create a new phase at any time within column B. This project schedule does not require phases. To remove the phase, simply delete the row. To create a new phase block in this row, enter a new Title in cell at right. To continue adding tasks to the phase above, enter a new row above this one and fill in the task data as in cell A9's instruction. Update the Phase details in cell at right based on cell A8's instruction. Continue navigating down column A cells to learn more. If you haven't added any new rows in this worksheet, you will find 2 additional sample phase blocks have been created for you in cells B20 and B26. Otherwise, navigate through column A cells to find the additional blocks. Repeat the instructions from cells A8 and A9 whenever you need to. | SCOPE 3 | A1 Electrical Rooms |  |  |  | 292 | 154 | 47.26% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.1 | Unit Substation LV Circuit Breakers (Primary Injection) | 46 | 46 | 3 | 138 | 0 | 100% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.2 | LV Distribution Panelboards | 11 | 0 | 4 | 44 | 44 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.3 | LV Panelboards | 49 | 0 | 1 | 49 | 49 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.4 | LV MCB Secondary Injection | 38 | 0 | 0.5 | 19 | 19 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.5 | LV Dry-Type Transformer | 6 | 0 | 1.25 | 7.5 | 7.5 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.6 | LV Bus Duct | 4 | 0 | 4 | 16 | 16 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.7 | LV Bus Duct MCB's (Secondary Injection) | 37 | 0 | 0.5 | 18.5 | 18.5 | 0% |  | 2025-07-01 | 2025-09-01
Sample phase title block | SCOPE 4 | A2 Electrical Rooms |  |  |  | 221.75 | 120.25 | 45.77% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.1 | Unit Substation LV Circuit Breakers (Primary Injection) | 33 | 33 | 3 | 99 | 0 | 100% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.2 | LV Distribution Panelboards | 12 | 0 | 4 | 48 | 48 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.3 | LV Panelboards | 43 | 0 | 1 | 43 | 43 | 0% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.4 | LV MCB Secondary Injection | 29 | 0 | 0.5 | 14.5 | 14.5 | 0% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.5 | LV Dry-Type Transformer | 3 | 2 | 1.25 | 3.75 | 1.25 | 66.67% |  | 2025-07-01 | 2025-09-01
| Task 1.6 | LV Bus Duct | 3 | 0 | 4 | 12 | 12 | 0% |  | 2025-07-01 | 2025-09-01 | 63
| Task 1.7 | LV Bus Duct MCB's (Secondary Injection) | 3 | 0 | 0.5 | 1.5 | 1.5 | 0% |  | 2025-07-01 | 2025-09-01
| SCOPE 5 | E Electrical Room |  |  |  | 709.7 | 338.35 | 52.32% |  | 2025-07-01 | 2025-09-01
| Task 1.1 | Unit Substation LV Circuit Breakers (Primary Injection) | 85 | 85 | 3 | 255 | 0 | 100% |  | 2025-07-01 | 2025-09-01
| Task 1.2 | LV Distribution Panelboards | 29 | 19 | 4 | 116 | 40 | 65.52% |  | 2025-07-01 | 2025-09-01
| Task 1.3 | LV Panelboards | 85 | 18 | 1 | 85 | 67 | 21.18% |  | 2025-07-01 | 2025-09-01
| Task 1.4 | LV MCB Secondary Injection | 90 | 0 | 0.5 | 45 | 45 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.5 | LV Dry-Type Transformer | 14 | 11 | 1.25 | 17.5 | 3.75 | 78.57% |  | 2025-07-01 | 2025-09-01
| Task 1.6 | LV Bus Duct | 12 | 2 | 4 | 48 | 40 | 16.67% |  | 2025-07-01 | 2025-09-01
| Task 1.7 | LV Bus Duct MCB's (Secondary Injection) | 281 | 0 | 0.5 | 140.5 | 140.5 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.8 | Electrode Room Point-to-Point | 5 | 2 | 0.3 | 1.5 | 0.9 | 40% |  | 2025-07-01 | 2025-09-01
| Task 1.9 | IT Room Point-to-Point | 4 | 0 | 0.3 | 1.2 | 1.2 | 0% |  | 2025-07-01 | 2025-09-01
| SCOPE 6 | F1 Electrical Room |  |  |  | 331.75 | 61.75 | 81.39% |  | 2025-07-01 | 2025-09-01
| Task 1.1 | Unit Substation LV Circuit Breakers (Primary Injection) | 90 | 90 | 3 | 270 | 0 | 100% |  | 2025-07-01 | 2025-09-01
| Task 1.2 | LV Distribution Panelboards | 7 | 0 | 4 | 28 | 28 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.3 | LV Panelboards | 22 | 0 | 1 | 22 | 22 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.4 | LV MCB Secondary Injection | 16 | 0 | 0.5 | 8 | 8 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.5 | LV Dry-Type Transformer | 3 | 0 | 1.25 | 3.75 | 3.75 | 0% |  | 2025-07-01 | 2025-09-01
| SCOPE 7 | F2 Electrical Room |  |  |  | 418.5 | 190.5 | 54.48% |  | 2025-07-01 | 2025-09-01
| Task 1.1 | Unit Substation LV Circuit Breakers (Primary Injection) | 76 | 76 | 3 | 228 | 0 | 100% |  | 2025-07-01 | 2025-09-01
| Task 1.2 | LV Distribution Panelboards | 27 | 0 | 4 | 108 | 108 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.3 | LV Panelboards | 23 | 0 | 1 | 23 | 23 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.4 | LV MCB Secondary Injection | 114 | 0 | 0.5 | 57 | 57 | 0% |  | 2025-07-01 | 2025-09-01
| Task 1.5 | LV Dry-Type Transformer | 2 | 0 | 1.25 | 2.5 | 2.5 | 0% |  | 2025-07-01 | 2025-09-01
|  |  | Total Project Progress: |  |  | 2159.7 | 1038.85 | 51.9%
This row marks the end of the Project Schedule. DO NOT enter anything in this row. Insert new rows ABOVE this one to continue building out your Project Schedule. | Insert new rows ABOVE this one
|  |  | Total | Remaining
|  | LV Circuit Breakers Primary Injection | 336 | 6
|  | LV Switchboards | 2 | 2
|  | LV ATS' | 9 | 6
|  | LV Distribution Panels | 91 | 72
|  | LV Panelboards | 249 | 231
|  | LV MCB Secondary Injection | 323 | 323
|  | LV Dry-Type Transformer | 34 | 21
|  | LV Bus Duct | 19 | 17
|  | LV Bus Duct MCB's (Secondary Injection) | 321 | 321

## Emergency Generator Dist
Emergency Generator Scope
Qty Bid | EQ Description | Drawing | QTY Complete | Hrs/unit | Total Hrs | QTY Remain. | Hours Remain | Progress | Notes
| 2.0 MW Generator & Distribution (Outdoor) | 1FO-E601
1 | 1F0EL-ESWB-01 (480Y/277V, 3000A) |  | 0 | 4 | 4 | 1 | 4 | 0%
3 | LV Circuit Breakers Primary Injection |  | 0 | 3 | 9 | 3 | 9 | 0%
Electrode Room Emergency Distribution
2 | LV ATS' (Hi-Potential & DLRO) |  | 1 | 4 | 8 | 1 | 4 | 50%
1 | LV Distribution Panel 1F0EL-EHDP-2 01 |  | 0 | 4 | 4 | 1 | 4 | 0%
8 | LV Panelboards |  | 0 | 1 | 8 | 8 | 8 | 0%
3 | LV MCB Secondary Injection |  | 0 | 0.5 | 1.5 | 3 | 1.5 | 0%
3 | LV Dry-Type Transformer |  | 0 | 1.25 | 3.75 | 3 | 3.75 | 0%
1.5 MW Generator & Distribution (Outdoor)
1 | 1F0AS-ESWB-02 (480Y/277V, 2500A) |  | 0 | 4 | 4 | 1 | 4 | 0%
3 | LV Circuit Breakers Primary Injection |  | 0 | 3 | 9 | 3 | 9 | 0%
A1 & A2 Electrical Room Emergency Distribution
2 | LV ATS' (Hi-Potential & DLRO) |  | 2 | 4 | 8 | 0 | 0 | 100%
1 | LV Distribution Panel 1F0AS-EHDP-2 02 |  | 0 | 4 | 4 | 1 | 4 | 0%
10 | LV Panelboards |  | 0 | 1 | 10 | 10 | 10 | 0%
2 | LV MCB Secondary Injection |  | 0 | 0.5 | 1 | 2 | 1 | 0%
1 | LV Dry-Type Transformer |  | 0 | 1.25 | 1.25 | 1 | 1.25 | 0%
F1 & F2 Electrical Room Emergency Distribution
1 | LV Distribution Panel 1F0FO-EHDP-2 01 |  | 0 | 4 | 4 | 1 | 4 | 0%
3 | LV ATS' (Hi-Potential & DLRO) |  | 0 | 4 | 12 | 3 | 12 | 0%
8 | LV Panelboards |  | 0 | 1 | 8 | 8 | 8 | 0%
3 | LV MCB Secondary Injection |  | 0 | 0.5 | 1.5 | 3 | 1.5 | 0%
56 | TOTALS |  | 3 |  | 101 | 53 | 89 | 11.88%
LV Distribution Panel = <1000 Amps Hi-Potential
LV Panelboard = >1000 Amps Insulation Resistance
LV MCB Secondary Injection = >250 Amps

## Datacenter Distribution
Datacenter Distribution Scope
Qty Bid | EQ Description | QTY Complete | Hrs/unit | Total Hrs | QTY Remain. | Hours Remain | Progress | Notes
Electrical Single Line 1FO-E653
2 | LV Isolation-Bypass ATS' (Hi-Potential & DLRO) | 0 | 4 | 8 | 2 | 8 | 0%
2 | LV Distribution Boards | 0 | 4 | 8 | 2 | 8 | 0%
8 | LV Circuit Breakers Primary Injection | 0 | 3 | 24 | 8 | 24 | 0%
2 | LV Distribution Panels | 0 | 4 | 8 | 2 | 8 | 0%
1 | LV Panelboards | 0 | 1 | 1 | 1 | 1 | 0%
Electrical Single Line 1FO-E654
2 | LV Large Dry-Type Transformer | 0 | 4 | 8 | 2 | 8 | 0%
2 | LV Distribution Boards | 0 | 4 | 8 | 2 | 8 | 0%
2 | LV Circuit Breakers Primary Injection | 0 | 3 | 6 | 2 | 6 | 0%
28 | LV MCB Secondary Injection | 0 | 0.5 | 14 | 28 | 14 | 0%
49 | TOTALS | 0 |  | 85 | 49 | 85 | 0%
LV Distribution Panel = <1000 Amps Hi-Potential
LV Panelboard = >1000 Amps Insulation Resistance
LV MCB Secondary Injection = >250 Amps

## A1 Electrical Room
A1 Elec Room Scope
Qty Bid | EQ Description | Drawing | QTY Complete | Hrs/unit | Total Hrs | QTY Remain. | Hours Remain | Progress | Notes
7 | 1F0AS-SS-A-01 USS 600V Breakers (Primary) | 1FO-E620 | 7 | 3 | 21 | 0 | 0 | 100%
3 | LV Distribution Panelboards |  | 0 | 4 | 12 | 3 | 12 | 0%
6 | LV Panelboards |  | 0 | 1 | 6 | 6 | 6 | 0%
15 | LV MCB Secondary Injection |  | 0 | 0.5 | 7.5 | 15 | 7.5 | 0%
1 | LV Bus Duct |  | 0 | 4 | 4 | 1 | 4 | 0%
9 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 4.5 | 9 | 4.5 | 0%
9 | 1F0AS-SS-A-02 USS 600V Breakers (Primary) | 1FO-E621 | 9 | 3 | 27 | 0 | 0 | 100%
3 | LV Distribution Panelboards |  | 0 | 4 | 12 | 3 | 12 | 0%
5 | LV Panelboards |  | 0 | 1 | 5 | 5 | 5 | 0%
11 | LV MCB Secondary Injection |  | 0 | 0.5 | 5.5 | 11 | 5.5 | 0%
4 | 1F0AS-SS-B-01 USS 600V Breakers (Primary) | 1FO-E624 | 4 | 3 | 12 | 0 | 0 | 100%
1 | LV Bus Duct |  | 0 | 4 | 4 | 1 | 4 | 0%
4 | 1F0AS-SS-B-02 USS 600V Breakers (Primary) | 1FO-E625 | 4 | 3 | 12 | 0 | 0 | 100%
3 | LV Panelboards |  | 0 | 1 | 3 | 3 | 3 | 0%
1 | LV Bus Duct |  | 0 | 4 | 4 | 1 | 4 | 0%
5 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 2.5 | 5 | 2.5 | 0%
4 | 1F0AS-SS-B-03 USS 600V Breakers (Primary) | 1FO-E626 | 4 | 3 | 12 | 0 | 0 | 100%
5 | LV Panelboards |  | 0 | 1 | 5 | 5 | 5 | 0%
1 | LV MCB Secondary Injection |  | 0 | 0.5 | 0.5 | 1 | 0.5 | 0%
1 | LV Bus Duct |  | 0 | 4 | 4 | 1 | 4 | 0%
23 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 11.5 | 23 | 11.5 | 0%
9 | 1F0AS-SS-B-04 USS 600V Breakers (Primary) | 1FO-E627 | 9 | 3 | 27 | 0 | 0 | 100%
2 | LV Distribution Panelboards |  | 0 | 4 | 8 | 2 | 8 | 0%
11 | LV Panelboards |  | 0 | 1 | 11 | 11 | 11 | 0%
8 | LV MCB Secondary Injection |  | 0 | 0.5 | 4 | 8 | 4 | 0%
2 | LV Dry-Type Transformer |  | 0 | 1.25 | 2.5 | 2 | 2.5 | 0%
9 | 1F0AS-SS-B-05 USS 600V Breakers (Primary) | 1FO-E628 | 9 | 3 | 27 | 0 | 0 | 100%
3 | LV Distribution Panelboards |  | 0 | 4 | 12 | 3 | 12 | 0%
19 | LV Panelboards |  | 0 | 1 | 19 | 19 | 19 | 0%
3 | LV MCB Secondary Injection |  | 0 | 0.5 | 1.5 | 3 | 1.5 | 0%
4 | LV Dry-Type Transformer |  | 0 | 1.25 | 5 | 4 | 5 | 0%
191 | TOTALS |  | 46 | 65.5 | 292 | 145 | 154 | 47.26%
LV Distribution Panel = <1000 Amps Hi-Potential
LV Panelboard = >1000 Amps Insulation Resistance
LV MCB Secondary Injection = >250 Amps

## A2 Electrical Room
A2 Elec Room Scope
Qty Bid | EQ Description | Drawing | QTY Complete | Hrs/unit | Total Hrs | QTY Remain. | Hours Remain | Progress | Notes
9 | 1F0AS-SS-C-01 USS 600V Breakers (Primary) | 1FO-E629 | 9 | 3 | 27 | 0 | 0 | 100%
4 | LV Distribution Panelboards |  | 0 | 4 | 16 | 4 | 16 | 0%
13 | LV Panelboards |  | 0 | 1 | 13 | 13 | 13 | 0%
5 | LV MCB Secondary Injection |  | 0 | 0.5 | 2.5 | 5 | 2.5 | 0%
3 | LV Dry-Type Transformer |  | 2 | 1.25 | 3.75 | 1 | 1.25 | 66.67%
[5 empty] | 0 | 0 | 0
5 | 1F0AS-SS-C-02 USS 600V Breakers (Primary) | 1FO-E630 | 5 | 3 | 15 | 0 | 0 | 100%
3 | LV Panelboards |  | 0 | 1 | 3 | 3 | 3 | 0%
2 | LV Bus Duct |  | 0 | 4 | 8 | 2 | 8 | 0%
3 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 1.5 | 3 | 1.5 | 0%
[5 empty] | 0 | 0 | 0
9 | 1F0AS-SS-C-03 USS 600V Breakers (Primary) | 1FO-E631 | 9 | 3 | 27 | 0 | 0 | 100%
6 | LV Distribution Panelboards |  | 0 | 4 | 24 | 6 | 24 | 0%
23 | LV Panelboards |  | 0 | 1 | 23 | 23 | 23 | 0%
21 | LV MCB Secondary Injection |  | 0 | 0.5 | 10.5 | 21 | 10.5 | 0%
[5 empty] | 0 | 0 | 0
10 | 1F0AS-SS-C-04 USS 600V Breakers (Primary) | 1FO-E632 | 10 | 3 | 30 | 0 | 0 | 100%
2 | LV Distribution Panelboards |  | 0 | 4 | 8 | 2 | 8 | 0%
4 | LV Panelboards |  | 0 | 1 | 4 | 4 | 4 | 0%
3 | LV MCB Secondary Injection |  | 0 | 0.5 | 1.5 | 3 | 1.5 | 0%
1 | LV Bus Duct |  | 0 | 4 | 4 | 1 | 4 | 0%
[5 empty] | 0 | 0 | 0
126 | TOTALS |  | 35 | 39.25 | 221.75 | 91 | 120.25 | 45.77%
LV Distribution Panel = <1000 Amps Hi-Potential
LV Panelboard = >1000 Amps Insulation Resistance
LV MCB Secondary Injection = >250 Amps

## E Electrical Room
E Elec Room Scope
Qty Bid | EQ Description | Drawing | QTY Complete | Hrs/unit | Total Hrs | QTY Remain. | Hours Remain | Progress | Notes
2 | 1F0EL-SS-A-01 USS 600V Breakers (Primary) | 1FO-E602 | 2 | 3 | 6 | 0 | 0 | 100%
2 | LV Panelboards |  | 1 | 1 | 2 | 1 | 1 | 50%
4 | LV MCB Secondary Injection |  | 0 | 0.5 | 2 | 4 | 2 | 0%
1 | LV Bus Duct |  | 1 | 4 | 4 | 0 | 0 | 100%
31 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 15.5 | 31 | 15.5 | 0%
2 | 1F0EL-SS-A-02 USS 600V Breakers (Primary) | 1FO-E603 | 2 | 3 | 6 | 0 | 0 | 100%
1 | LV Bus Duct |  | 0 | 4 | 4 | 1 | 4 | 0%
33 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 16.5 | 33 | 16.5 | 0%
5 | 1F0EL-SS-A-03 USS 600V Breakers (Primary) | 1FO-E604 | 5 | 3 | 15 | 0 | 0 | 100%
1 | LV Bus Duct |  | 0 | 4 | 4 | 1 | 4 | 0%
22 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 11 | 22 | 11 | 0%
2 | 1F0EL-SS-A-04 USS 600V Breakers (Primary) | 1FO-E605 | 2 | 3 | 6 | 0 | 0 | 100%
1 | LV Bus Duct |  | 0 | 4 | 4 | 1 | 4 | 0%
18 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 9 | 18 | 9 | 0%
5 | 1F0EL-SS-B-01 USS 600V Breakers (Primary) | 1FO-E607 | 5 | 3 | 15 | 0 | 0 | 100%
1 | LV Distribution Panelboards |  | 0 | 4 | 4 | 1 | 4 | 0%
6 | LV Panelboards |  | 0 | 1 | 6 | 6 | 6 | 0%
5 | LV MCB Secondary Injection |  | 0 | 0.5 | 2.5 | 5 | 2.5 | 0%
2 | LV Bus Duct |  | 0 | 4 | 8 | 2 | 8 | 0%
36 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 18 | 36 | 18 | 0%
9 | 1F0EL-SS-B-02 USS 600V Breakers (Primary) | 1FO-E608 | 9 | 3 | 27 | 0 | 0 | 100%
5 | LV Distribution Panelboards |  | 5 | 4 | 20 | 0 | 0 | 100%
10 | LV Panelboards |  | 10 | 1 | 10 | 0 | 0 | 100%
14 | LV MCB Secondary Injection |  | 0 | 0.5 | 7 | 14 | 7 | 0%
2 | LV Dry-Type Transformer |  | 2 | 1.25 | 2.5 | 0 | 0 | 100%
9 | 1F0EL-SS-B-03 USS 600V Breakers (Primary) | 1FO-E609 | 9 | 3 | 27 | 0 | 0 | 100%
5 | LV Distribution Panelboards |  | 3 | 4 | 20 | 2 | 8 | 60%
20 | LV Panelboards |  | 0 | 1 | 20 | 20 | 20 | 0%
12 | LV MCB Secondary Injection |  | 0 | 0.5 | 6 | 12 | 6 | 0%
6 | LV Dry-Type Transformer |  | 3 | 1.25 | 7.5 | 3 | 3.75 | 50%
13 | 1F0EL-SS-B-04 USS 600V Breakers (Primary) | 1FO-E610 | 13 | 3 | 39 | 0 | 0 | 100%
6 | LV Distribution Panelboards |  | 2 | 4 | 24 | 4 | 16 | 33.33%
6 | LV Panelboards |  | 0 | 1 | 6 | 6 | 6 | 0%
23 | LV MCB Secondary Injection |  | 0 | 0.5 | 11.5 | 23 | 11.5 | 0%
9 | 1F0EL-SS-C-01 USS 600V Breakers (Primary) | 1FO-E611 | 9 | 3 | 27 | 0 | 0 | 100%
5 | LV Distribution Panelboards |  | 4 | 4 | 20 | 1 | 4 | 80%
13 | LV Panelboards |  | 2 | 1 | 13 | 11 | 11 | 15.38%
8 | LV MCB Secondary Injection |  | 0 | 0.5 | 4 | 8 | 4 | 0%
2 | LV Dry-Type Transformer |  | 2 | 1.25 | 2.5 | 0 | 0 | 100%
709.7
2 | 1F0EL-SS-C-02 USS 600V Breakers (Primary) | 1FO-E612 | 2 | 3 | 6 | 0 | 0 | 100%
1 | LV Bus Duct |  | 1 | 4 | 4 | 0 | 0 | 100%
34 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 17 | 34 | 17 | 0%
2 | 1F0EL-SS-C-03 USS 600V Breakers (Primary) | 1FO-E613 | 2 | 3 | 6 | 0 | 0 | 100%
1 | LV Panelboards |  | 0 | 1 | 1 | 1 | 1 | 0%
1 | LV Bus Duct |  |  | 4 | 4 | 1 | 4 | 0%
53 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 26.5 | 53 | 26.5 | 0%
5 | 1F0EL-SS-D-02 USS 600V Breakers (Primary) | 1FO-E616 | 5 | 3 | 15 | 0 | 0 | 100%
1 | LV Panelboards |  | 0 | 1 | 1 | 1 | 1 | 0%
2 | LV Bus Duct |  | 0 | 4 | 8 | 2 | 8 | 0%
17 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 8.5 | 17 | 8.5 | 0%
11 | 1F0EL-SS-D-01 USS 600V Breakers (Primary) | 1FO-E617 | 11 | 3 | 33 | 0 | 0 | 100%
3 | LV Distribution Panelboards |  | 3 | 4 | 12 | 0 | 0 | 100%
6 | LV Panelboards |  | 1 | 1 | 6 | 5 | 5 | 16.67%
13 | LV MCB Secondary Injection |  | 0 | 0.5 | 6.5 | 13 | 6.5 | 0%
2 | LV Bus Duct |  | 0 | 4 | 8 | 2 | 8 | 0%
37 | LV Bus Duct MCB's (Secondary Injection) |  | 0 | 0.5 | 18.5 | 37 | 18.5 | 0%
9 | 1F0EL-SS-D-03 USS 600V Breakers (Primary) | 1FO-E619 | 9 | 3 | 27 | 0 | 0 | 100%
4 | LV Distribution Panelboards |  | 2 | 4 | 16 | 2 | 8 | 50%
20 | LV Panelboards |  | 4 | 1 | 20 | 16 | 16 | 20%
11 | LV MCB Secondary Injection |  | 0 | 0.5 | 5.5 | 11 | 5.5 | 0%
4 | LV Dry-Type Transformer |  | 4 | 1.25 | 5 | 0 | 0 | 100%
Equipment Grounding P-T-P
5 | Electrode Room P-T-P |  | 2 | 0.3 | 1.5 | 3 | 0.9 | 40%
4 | IT Room P-T-P |  | 0 | 0.3 | 1.2 | 4 | 1.2 | 0%
605 | TOTALS |  | 137 | 130.1 | 709.7 | 468 | 338.35 | 52.32%
LV Distribution Panel = <1000 Amps Hi-Potential
LV Panelboard = >1000 Amps Insulation Resistance
LV MCB Secondary Injection = >250 Amps

## F1 Electrical Room
F1 Elec Room Scope
Qty Bid | EQ Description | Drawing | QTY Complete | Hrs/unit | Total Hrs | QTY Remain. | Hours Remain | Progress | Notes
9 | 1F0FO-SS-A-01 USS 600V Breakers (Primary) | 1FO-E633 | 9 | 3 | 27 | 0 | 0 | 100%
| LV Distribution Panelboards | [7 empty] | Future
| LV MCB Secondary Injection | [7 empty] | Future
9 | 1F0FO-SS-A-02 USS 600V Breakers (Primary) | 1FO-E634 | 9 | 3 | 27 | 0 | 0 | 100%
1 | LV Distribution Panelboards |  | 0 | 4 | 4 | 1 | 4 | 0%
9 | LV Panelboards |  | 0 | 1 | 9 | 9 | 9 | 0%
5 | LV MCB Secondary Injection |  | 0 | 0.5 | 2.5 | 5 | 2.5 | 0%
9 | 1F0FO-SS-A-03 USS 600V Breakers (Primary) | 1FO-E635 | 9 | 3 | 27 | 0 | 0 | 100%
3 | LV Distribution Panelboards |  | 0 | 4 | 12 | 3 | 12 | 0%
13 | LV Panelboards |  | 0 | 1 | 13 | 13 | 13 | 0%
5 | LV MCB Secondary Injection |  | 0 | 0.5 | 2.5 | 5 | 2.5 | 0%
1 | LV Dry-Type Transformer |  | 0 | 1.25 | 1.25 | 1 | 1.25 | 0%
9 | 1F0FO-SS-A-04 USS 600V Breakers (Primary) | 1FO-E636 | 9 | 3 | 27 | 0 | 0 | 100%
| LV Distribution Panelboards | [7 empty] | Future
| LV MCB Secondary Injection | [7 empty] | Future
9 | 1F0FO-SS-A-05 USS 600V Breakers (Primary) | 1FO-E637 | 9 | 3 | 27 | 9 | 27 | 0%
| LV Distribution Panelboards | [7 empty] | Future
| LV MCB Secondary Injection | [7 empty] | Future
9 | 1F0FO-SS-B-01 USS 600V Breakers (Primary) | 1FO-E638 | 9 | 3 | 27 | 0 | 0 | 100%
2 | LV Dry-Type Transformer |  | 0 | 1.25 | 2.5 | 2 | 2.5 | 0%
9 | 1F0FO-SS-B-02 USS 600V Breakers (Primary) | 1FO-E639 | 9 | 3 | 27 | 0 | 0 | 100%
3 | LV Distribution Panelboards |  | 0 | 4 | 12 | 3 | 12 | 0%
6 | LV MCB Secondary Injection |  | 0 | 0.5 | 3 | 6 | 3 | 0%
9 | 1F0FO-SS-B-03 USS 600V Breakers (Primary) | 1FO-E640 | 9 | 3 | 27 | 0 | 0 | 100%
| LV Distribution Panelboards | [7 empty] | Future
| LV MCB Secondary Injection | [7 empty] | Future
9 | 1F0FO-SS-B-04 USS 600V Breakers (Primary) | 1FO-E641 | 9 | 3 | 27 | 0 | 0 | 100%
| LV Distribution Panelboards | [7 empty] | Future
| LV MCB Secondary Injection | [7 empty] | Future
9 | 1F0FO-SS-B-05 USS 600V Breakers (Primary) | 1FO-E642 | 9 | 3 | 27 | 9 | 27 | 0%
| LV Distribution Panelboards | [7 empty] | Future
| LV MCB Secondary Injection | [7 empty] | Future
138 | TOTALS |  | 90 | 48 | 331.75 | 48 | 115.75 | 65.11%
LV Distribution Panel = <1000 Amps Hi-Potential
LV Panelboard = >1000 Amps Insulation Resistance
LV MCB Secondary Injection = >250 Amps

## F2 Eletrical Room
F2 Elec Room Scope
Qty Bid | EQ Description | Drawing | QTY Complete | Hrs/unit | Total Hrs | QTY Remain. | Hours Remain | Progress | Notes
9 | 1F0FO-SS-C-01 USS 600V Breakers (Primary) | 1FO-E643 | 9 | 3 | 27 | 0 | 0 | 100%
3 | LV Distribution Panelboards |  | 0 | 4 | 12 | 3 | 12 | 0%
9 | LV Panelboards |  | 0 | 1 | 9 | 9 | 9 | 0%
6 | LV MCB Secondary Injection |  | 0 | 0.5 | 3 | 6 | 3 | 0%
2 | LV Dry-Type Transformer |  | 0 | 1.25 | 2.5 | 2 | 2.5 | 0%
0
13 | 1F0FO-SS-C-02 USS 600V Breakers (Primary) | 1FO-E644 | 13 | 3 | 39 | 0 | 0 | 100%
3 | LV Distribution Panelboards |  | 0 | 4 | 12 | 3 | 12 | 0%
9 | LV Panelboards |  | 0 | 1 | 9 | 9 | 9 | 0%
8 | LV MCB Secondary Injection |  | 0 | 0.5 | 4 | 8 | 4 | 0%
0
9 | 1F0FO-SS-C-03 USS 600V Breakers (Primary) | 1FO-E645 | 9 | 3 | 27 | 0 | 0 | 100%
4 | LV Distribution Panelboards |  | 0 | 4 | 16 | 4 | 16 | 0%
20 | LV MCB Secondary Injection |  | 0 | 0.5 | 10 | 20 | 10 | 0%
0
9 | 1F0FO-SS-C-04 USS 600V Breakers (Primary) | 1FO-E646 | 9 | 3 | 27 | 0 | 0 | 100%
1 | LV Distribution Panelboards |  | 0 | 4 | 4 | 1 | 4 | 0%
5 | LV Panelboards |  | 0 | 1 | 5 | 5 | 5 | 0%
11 | LV MCB Secondary Injection |  | 0 | 0.5 | 5.5 | 11 | 5.5 | 0%
0
9 | 1F0FO-SS-D-01 USS 600V Breakers (Primary) | 1FO-E647 | 9 | 3 | 27 | 0 | 0 | 100%
4 | LV Distribution Panelboards |  | 0 | 4 | 16 | 4 | 16 | 0%
20 | LV MCB Secondary Injection |  | 0 | 0.5 | 10 | 20 | 10 | 0%
0
9 | 1F0FO-SS-D-02 USS 600V Breakers (Primary) | 1FO-E648 | 9 | 3 | 27 | 0 | 0 | 100%
4 | LV Distribution Panelboards |  | 0 | 4 | 16 | 4 | 16 | 0%
18 | LV MCB Secondary Injection |  | 0 | 0.5 | 9 | 20 | 10 | 0%
0
9 | 1F0FO-SS-D-03 USS 600V Breakers (Primary) | 1FO-E649 | 9 | 3 | 27 | 0 | 0 | 100%
4 | LV Distribution Panelboards |  | 0 | 4 | 16 | 4 | 16 | 0%
16 | LV MCB Secondary Injection |  | 0 | 0.5 | 8 | 20 | 10 | 0%
0
9 | 1F0FO-SS-D-04 USS 600V Breakers (Primary) |  | 9 | 3 | 27 | 0 | 0 | 100%
4 | LV Distribution Panelboards |  | 0 | 4 | 16 | 4 | 16 | 0%
15 | LV MCB Secondary Injection |  | 0 | 0.5 | 7.5 | 15 | 7.5 | 0%
242 | TOTALS |  | 76 | 64.25 | 418.5 | 166 | 193.5 | 53.76%
LV Distribution Panel = <1000 Amps Hi-Potential
LV Panelboard = >1000 Amps Insulation Resistance
LV MCB Secondary Injection = >250 Amps

## RESA MV Breaker Test Results (hidden)
www.resapower.com
MV BREAKER TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  |  | 559082 |  |  |  |  | DATE: |  |  |  | 2025-01-21 |  |  |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: |  |  |  | AP/TD | [9 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  |  | TPG CAT MODERNIZATION |  |  |  |  | APPROVED BY: |  |  |  | J. SWENSON | [9 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | CONTACT RESISTANCE |  | INSULATION RESISTANCE |  | VACUUM BOTTLE INTEGRITY |  | OVERPOTENTIAL |  |  | INSULATION RESISTANCE |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
www.resapower.com
MV BREAKER TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  |  | 559082 |  |  |  |  | DATE: |  |  |  | 2025-01-21 |  |  |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: |  |  |  | AP/TD | [9 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  |  | TPG CAT MODERNIZATION |  |  |  |  | APPROVED BY: |  |  |  | J. SWENSON | [9 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | CONTACT RESISTANCE |  | INSULATION RESISTANCE |  | VACUUM BOTTLE INTEGRITY |  | OVERPOTENTIAL |  |  | INSULATION RESISTANCE |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
ACCEPTABLE
NOT ACCEPTABLE
SEE NOTES
Note on CN9: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AF14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AS14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on CN64: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AC69: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL69: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P

## RESA Relay Test Results (hidden)
www.resapower.com
MV BREAKER TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  |  | 559082 |  |  |  |  | DATE: |  |  |  | 2025-01-21 |  |  |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: |  |  |  | AP/TD | [9 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  |  | TPG CAT MODERNIZATION |  |  |  |  | APPROVED BY: |  |  |  | J. SWENSON | [9 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | CONTACT RESISTANCE |  | INSULATION RESISTANCE |  | VACUUM BOTTLE INTEGRITY |  | OVERPOTENTIAL |  |  | INSULATION RESISTANCE |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
www.resapower.com
MV BREAKER TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  |  | 559082 |  |  |  |  | DATE: |  |  |  | 2025-01-21 |  |  |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: |  |  |  | AP/TD | [9 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  |  | TPG CAT MODERNIZATION |  |  |  |  | APPROVED BY: |  |  |  | J. SWENSON | [9 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | WINDING RESISTANCE |  | INSULATION RESISTANCE |  | TURNS RATIO |  | BURDEN |  |  | ACCURACY CLASS |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
ACCEPTABLE
NOT ACCEPTABLE
SEE NOTES
Note on CN9: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AC14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on CN66: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AC71: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL71: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P

## RESA CT Test Results (hidden)
www.resapower.com
MV-01 CT TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  |  | 559082 |  |  |  |  | DATE: |  |  |  | 2025-01-21 |  |  |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: |  |  |  | AP/TD | [9 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  |  | TPG CAT MODERNIZATION |  |  |  |  | APPROVED BY: |  |  |  | J. SWENSON | [9 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | WINDING RESISTANCE |  | INSULATION RESISTANCE |  | TURNS RATIO |  | BURDEN |  |  | ACCURACY CLASS |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
www.resapower.com
MV-01 CT TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: | [9 empty] | DATE: | [8 empty] | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: | [13 empty] | MAINTENANCE TEST
SITE/LOCATION: | [9 empty] | APPROVED BY: | [13 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | WINDING RESISTANCE |  | INSULATION RESISTANCE |  | TURNS RATIO |  | BURDEN |  |  | ACCURACY CLASS |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
www.resapower.com
MV BREAKER TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  |  | 559082 |  |  |  |  | DATE: |  |  |  | 2025-01-21 |  |  |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: |  |  |  | AP/TD | [9 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  |  | TPG CAT MODERNIZATION |  |  |  |  | APPROVED BY: |  |  |  | J. SWENSON | [9 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | WINDING RESISTANCE |  | INSULATION RESISTANCE |  | TURNS RATIO |  | BURDEN |  |  | ACCURACY CLASS |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
www.resapower.com
MV BREAKER TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  |  | 559082 |  |  |  |  | DATE: |  |  |  | 2025-01-21 |  |  |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: |  |  |  | AP/TD | [9 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  |  | TPG CAT MODERNIZATION |  |  |  |  | APPROVED BY: |  |  |  | J. SWENSON | [9 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | WINDING RESISTANCE |  | INSULATION RESISTANCE |  | TURNS RATIO |  | BURDEN |  |  | ACCURACY CLASS |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
ACCEPTABLE
NOT ACCEPTABLE
SEE NOTES
Note on CN9: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AC14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on CN64: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AC69: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL69: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on CN119: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AC124: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL124: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on CN174: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AC179: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL179: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P

## RESA PT Test Results (hidden)
www.resapower.com
MV BREAKER TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  |  | 559082 |  |  |  |  | DATE: |  |  |  | 2025-01-21 |  |  |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: |  |  |  | AP/TD | [9 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  |  | TPG CAT MODERNIZATION |  |  |  |  | APPROVED BY: |  |  |  | J. SWENSON | [9 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | CONTACT RESISTANCE |  | INSULATION RESISTANCE |  | VACUUM BOTTLE INTEGRITY |  | OVERPOTENTIAL |  |  | INSULATION RESISTANCE |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
www.resapower.com
MV BREAKER TEST RESULT SUMMARY | [22 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  |  | 559082 |  |  |  |  | DATE: |  |  |  | 2025-01-21 |  |  |  |  | TESTING STANDARD |  |  | P |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  |  | STURGEON ELECTRIC |  |  |  |  | TESTED BY: |  |  |  | AP/TD | [9 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  |  | TPG CAT MODERNIZATION |  |  |  |  | APPROVED BY: |  |  |  | J. SWENSON | [9 empty] | PROOF TEST
BREAKER NAMEPLATE DATA
MANUFACTURER: |  |  | EATON |  |  | RATED AMPS: |  | 1200 |  |  |  | BIL (kV): |  |  | 10 |  | INTERRUPT RATING: |  |  | 40 kA |  | CLOSE/CHG VOLTAGE: |  |  |  | 120 VAC
TYPE: |  |  | 15VCP-W40 |  |  | RATED VOLTS: |  | 15 kV |  |  |  | WITHSTAND VOLTAGE: |  |  | 95 kV |  | INTERRUPT TIME: |  |  | 50 ms |  | TRIP CKT VOLTAGE: |  |  |  | 120 VAC (CAP TRIP)
TEST & INSPECTION CHECKLIST
| DEVICE ID | SERIAL NUMBER |  | LOAD SERVED |  |  | WINDING RESISTANCE |  | INSULATION RESISTANCE |  | TURNS RATIO |  | BURDEN |  |  | ACCURACY CLASS |  | TIMING TESTS |  | FUNCTIONAL TESTING | NOTES
ACCEPTABLE
NOT ACCEPTABLE
SEE NOTES
Note on CN9: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AC14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on CN64: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AC69: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL69: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P

## RESA LV Cable Test Results (hidden)
#VALUE! | [37 empty] | www.resapower.com
LV CABLE TEST FORM | [33 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  | 559082 |  |  |  | DATE: | [8 empty] | 2025-01-11 | [7 empty] | TESTING STANDARD | [6 empty] | P |  |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  | STURGEON ELECTRIC |  |  |  | TESTED BY: | [8 empty] | AP/TD | [17 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  | TPG CAT MODERNIZATION |  |  |  | APPROVED BY: | [8 empty] | J. SWENSON | [17 empty] | PROOF TEST
CABLE NAMEPLATE DATA
CABLE INSULATION | [6 empty] | JACKET | [5 empty] | LSZH, CPE | [10 empty] | CONDUCTOR MATERIAL
MANUFACTURER |  |  |  |  | LOCATION |  |  |  | P |  | INDOOR | [5 empty] | P |  |  | OUTDOOR |  |  |  | TEMPERATURE RATING
TEST & INSPECTION CHECKLIST
| DESCRIPTION | [10 empty] | PASS |  |  | FAIL | N/A |  |  | NOTES
| VISUAL INSPECTION | [10 empty] | P | [6 empty] | NO VISIBLE DAMAGE
| PHASING OK | [10 empty] | P | [6 empty] | VERIFIED WITH MULTIMETER
| TERMINATIONS - CONDITION - INSTALLATION | [10 empty] | P | [6 empty] | PER MANUFACTURER SPECS
| TORQUE MARKS PRESENT | [10 empty] | P | [6 empty] | VERIFIED
| DRAWING NUMBER: | [14 empty] | REVISION:
INSULATION RESISTANCE & CONTINUITY TEST
| CABLE RUN DESCRIPTION | [17 empty] | CONDUCTOR CONT. VERIFIED TO GROUND | [6 empty] | INSULATION RESISTANCE TEST @ 1kV DC
| CABLE ID | ORIGIN |  | DESTINATION |  | INSULATION |  |  |  | SETS |  |  |  | FORMATION |  |  |  |  | A |  | B | C | G |  | N | A-G | B-G |  | C-G |  | A-N |  |  | B-N |  |  | C-N | A-B |  | B-C | C-A
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  | - | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
| EQUIPMENT # |  | 155643WFDV | [7 empty] | TEMPERATURE | [6 empty] | 25 |  |  | °C | HUMIDITY |  |  |  | 22 |  | % |  | RESULTS GΩ
[29 empty] | RESULTS |  |  |  | P |  |  | PASS |  |  | FAIL
#VALUE! | [37 empty] | www.resapower.com
LV CABLE TEST FORM | [33 empty] | TF-03 Rev.8
JOB NUMBER: |  |  |  | 559082 |  |  |  | DATE: | [8 empty] | 2025-01-11 | [7 empty] | TESTING STANDARD | [6 empty] | P |  |  | ACCEPTANCE TEST
CLIENT NAME: |  |  |  | STURGEON ELECTRIC |  |  |  | TESTED BY: | [8 empty] | AP/TD | [17 empty] | MAINTENANCE TEST
SITE/LOCATION: |  |  |  | TPG CAT MODERNIZATION |  |  |  | APPROVED BY: | [8 empty] | J. SWENSON | [17 empty] | PROOF TEST
CABLE NAMEPLATE DATA
CABLE INSULATION | [6 empty] | JACKET | [5 empty] | LSZH, CPE | [10 empty] | CONDUCTOR MATERIAL
MANUFACTURER |  |  |  |  | LOCATION |  |  |  | P |  | INDOOR | [5 empty] | P |  |  | OUTDOOR |  |  |  | TEMPERATURE RATING
TEST & INSPECTION CHECKLIST
| DESCRIPTION | [10 empty] | PASS |  |  | FAIL | N/A |  |  | NOTES
| VISUAL INSPECTION | [10 empty] | P | [6 empty] | NO VISIBLE DAMAGE
| PHASING OK | [10 empty] | P | [6 empty] | VERIFIED WITH MULTIMETER
| TERMINATIONS - CONDITION - INSTALLATION | [10 empty] | P | [6 empty] | PER MANUFACTURER SPECS
| TORQUE MARKS PRESENT | [10 empty] | P | [6 empty] | VERIFIED
| DRAWING NUMBER: | [14 empty] | REVISION:
INSULATION RESISTANCE & CONTINUITY TEST
| CABLE RUN DESCRIPTION | [17 empty] | CONDUCTOR CONT. VERIFIED TO GROUND | [6 empty] | INSULATION RESISTANCE TEST @ 1kV DC
| CABLE ID | ORIGIN |  | DESTINATION |  | INSULATION |  |  |  | SETS |  |  |  | FORMATION |  |  |  |  | A |  | B | C | G |  | N | A-G | B-G |  | C-G |  | A-N |  |  | B-N |  |  | C-N | A-B |  | B-C | C-A
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
[19 empty] | P |  | P | P | P |  |  | >2.2 | >2.2 |  | >2.2 |  | - |  |  | - |  |  | - | >2.2 |  | >2.2 | >2.2
| EQUIPMENT # |  | 155643WFDV | [7 empty] | TEMPERATURE | [6 empty] | 25 |  |  | °C | HUMIDITY |  |  |  | 22 |  | % |  | RESULTS GΩ
[29 empty] | RESULTS |  |  |  | P |  |  | PASS |  |  | FAIL
Note on CN9: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AF14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AS14: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL18: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AO18: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AR18: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL19: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AO19: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AR19: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL20: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AO20: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AR20: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL21: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AO21: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AR21: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU29: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX29: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA29: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD29: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU30: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX30: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA30: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD30: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU31: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX31: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA31: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD31: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU32: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX32: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA32: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD32: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU33: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX33: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA33: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD33: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU34: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX34: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA34: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD34: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU35: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX35: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA35: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD35: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU36: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX36: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA36: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD36: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU37: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX37: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA37: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD37: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU38: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX38: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA38: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD38: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU39: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX39: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA39: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD39: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU40: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX40: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA40: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD40: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU41: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX41: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA41: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD41: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU42: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX42: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA42: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD42: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU43: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX43: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA43: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD43: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU44: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX44: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA44: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD44: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU45: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX45: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA45: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD45: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU46: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX46: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA46: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD46: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU47: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX47: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA47: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD47: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU48: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX48: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA48: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD48: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU49: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX49: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA49: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD49: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU50: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX50: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA50: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD50: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU51: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX51: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA51: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD51: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on CN65: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AF70: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AS70: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL74: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AO74: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AR74: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL75: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AO75: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AR75: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL76: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AO76: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AR76: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AL77: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AO77: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AR77: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU85: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX85: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA85: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD85: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG85: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU86: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX86: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA86: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD86: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG86: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU87: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX87: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA87: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD87: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG87: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU88: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX88: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA88: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD88: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG88: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU89: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX89: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA89: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD89: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG89: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU90: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX90: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA90: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD90: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG90: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU91: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX91: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA91: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD91: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG91: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU92: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX92: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA92: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD92: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG92: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU93: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX93: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA93: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD93: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG93: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU94: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX94: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA94: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD94: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG94: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU95: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX95: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA95: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD95: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG95: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU96: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX96: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA96: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD96: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG96: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU97: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX97: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA97: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD97: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG97: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU98: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX98: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA98: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD98: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG98: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU99: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX99: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA99: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD99: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG99: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU100: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX100: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA100: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD100: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG100: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU101: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX101: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA101: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD101: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG101: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU102: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX102: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA102: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD102: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG102: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU103: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX103: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA103: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD103: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG103: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU104: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX104: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA104: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD104: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG104: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU105: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX105: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA105: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD105: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG105: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU106: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX106: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA106: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD106: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG106: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AU107: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on AX107: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BA107: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BD107: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P
Note on BG107: Tim Gannon: Font for Check Marks is Wingdings 2. Use a capital 'P' to create a check. 'P' = P